## WAN
SN | Ticket No | W/O | Date | NOC WAN Engineer | Alert Type | Issue Type | Initial Findings | Node ID | Cabinet Asset Field Tag | Location | Coordinates | Area Category | Severity | Fault Notification Date and Time (dd/mm/yy hh:mm) | Fault Response Date and Time (dd/mm/yy hh:mm) | FRT Fault Response Time (Minutes) | Actual Start Date and Time (dd/mm/yy hh:mm) | Actual Finish Date and Time (dd/mm/yy hh:mm) | ART Active Repair Time (Minutes) | TRT Total Repair Time (Minutes) | Action Taken | Status | Fault Attribution | FA Class | FA (Fault Attraction) Notes | Remarks | Field Engineer
1 | NA | NA | 2026-02-01 | - | Node Down | Network down | FLM visited the site and confirmed that Kahramaa power was not available at the cabinet. | P010-ENC61-CE-01 |  | Zone 57 | 51.4699752, 25.170097 | Outside Doha | Critical | 2026-02-01 08:39 | 2026-02-01 08:39 | 0 | 2026-02-01 08:39 | 2026-02-01 13:57 | 318 | 318 | Power was restored by Kahramaa after 5 hours and 17 minutes.Network was up. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
2 | NA | NA | 2026-02-02 | - | Node Down | Network down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-02 13:04 | 2026-02-02 13:04 | 0 | 2026-02-02 13:04 | 2026-02-02 13:08 | 4 | 4 | Link restored after 4 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
3 | NA | NA | 2026-02-02 | - | Node Down | Network down | network went down due to system upgrade | P008C2-Enc09-CE01 |  | - | - | - | Critical | 2026-02-02 06:49 | 2026-02-02 06:49 | 0 | 2026-02-02 06:49 | 2026-02-02 06:50 | 1 | 1 | Escalated to Salam Tech team (Imran) on phone and rebooted the system | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
4 | NA | NA | 2026-02-04 | Vishnu | Node Down | Device Down | Power failure detected at the site | Sal-ENC38-CE-01 |  | Zone 83 | 51.1144427, 25.069908 | Outside Doha | Critical | 2026-02-04 07:00 | 2026-02-04 07:00 | 0 | 2026-02-04 08:00 | 2026-02-04 13:52 | 352 | 412 | The Kahramaa team is currently performing maintenance on the main electrical poles in the area.Expected Completion: Restoration is anticipated by 2:00 PM. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
5 | NA | NA | 2026-02-05 | - | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-05 12:47 | 2026-02-05 12:47 | 0 | 2026-02-05 12:47 | 2026-02-05 12:50 | 3 | 3 | Link restored after 3 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
6 | NA | NA | 2026-02-05 | - | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-05 14:25 | 2026-02-05 14:25 | 0 | 2026-02-05 14:25 | 2026-02-05 14:36 | 11 | 11 | Link restored after 11 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
7 | NA | NA | 2026-02-06 | Vishnu | Node Down | Device Down | UPS was not giving output | P010-ENC61–CE-01 |  | Zone 57 | 51.4699752, 25.170097 | Outside Doha | Critical | 2026-02-06 09:36 | 2026-02-06 09:36 | 0 | 2026-02-06 11:01 | 2026-02-06 11:08 | 7 | 92 | Issue resolved after restarting UPS | Completed | Maintainer | N/a | N/a | Network Back Online
8 | NA | NA | 2026-02-07 | Vishnu | Node Down | Device Down | Noticed no power on Main breakers/Terminals | P023C1-ENC01–CE -01 |  | Zone 91 | 51.583897, 25.111748 | Outside Doha | Critical | 2026-02-07 11:25 | 2026-02-07 11:25 | 0 | 2026-02-07 12:02 | 2026-02-07 13:13 | 71 | 108 | Power supply restored by Kahrama staff.KAHRAMAA reference No. 261100005225 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
9 | NA | NA | 2026-02-07 | Vishnu | Node Down | Device Down | Noticed no power on Main breakers/Terminals | P023C1-ENC01–UPE -01 |  | Zone 91 | 51.583897, 25.111748 | Outside Doha | Critical | 2026-02-07 11:25 | 2026-02-07 11:25 | 0 | 2026-02-07 12:02 | 2026-02-07 13:13 | 71 | 108 | Power supply restored by Kahrama staff.KAHRAMAA reference No. 261100005225 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
10 | NA | NA | 2026-02-08 | Salem/Amr | Node Down | Device Down | MCB was tripped at site | SAL-ENC50–CE -01 |  | Zone 96 | 50.9993542, 24.9513076 | Outside Doha | Critical | 2026-02-08 12:29 | 2026-02-08 12:29 | 0 | 2026-02-08 13:34 | 2026-02-08 14:00 | 26 | 91 | team turned on the CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online
11 | NA | NA | 2026-02-09 | Salem/Amr | Node Down | Device Down | Link went down | P008C3-ENC01–CE -01 |  | Zone 55 | 51.4801647, 25.2614822 | Outside Doha | Critical | 2026-02-09 15:06 | 2026-02-09 15:06 | 0 | 2026-02-09 15:06 | 2026-02-09 15:08 | 2 | 2 | Escalated to Salam Tech team (Imran) on phone and rebooted the system | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
12 | NA | NA | 2026-02-09 | Salem/Amr | Node Down | Device Down | Link went down | P008C3-ENC25–CE -01 |  | Zone 56 | 51.50261, 25.2341068 | Outside Doha | Critical | 2026-02-09 15:43 | 2026-02-09 15:43 | 0 | 2026-02-09 15:43 | 2026-02-09 15:45 | 2 | 2 | Escalated to Salam Tech team (Imran) on phone and rebooted the system | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
13 | NA | NA | 2026-02-10 | Salem/Amr | Node Down | Link Down | MCB was tripped at site | P005-ENC410-CE-01 |  | Zone 56 | 51.399465, 25.3102445 | Outside Doha | Critical | 2026-02-10 13:39 | 2026-02-10 13:39 | 0 | 2026-02-10 14:14 | 2026-02-10 15:52 | 98 | 133 | Team turned on the CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online
14 | NA | NA | 2026-02-10 | Salem/Amr | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-10 16:19 | 2026-02-10 16:19 | 0 | 2026-02-10 16:19 | 2026-02-10 16:26 | 7 | 7 | Link went down and restored after 7 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
15 | NA | NA | 2026-02-11 | Salem/Amr | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-11 12:59 | 2026-02-11 12:59 | 0 | 2026-02-11 12:59 | 2026-02-11 13:09 | 10 | 10 | Link went down and restored after 10 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
16 | NA | NA | 2026-02-11 | Salem/Amr | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-11 13:10 | 2026-02-11 13:10 | 0 | 2026-02-11 13:10 | 2026-02-11 13:18 | 8 | 8 | Link went down and restored after 8 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
17 | NA | NA | 2026-02-11 | Salem/Amr | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-11 16:09 | 2026-02-11 16:09 | 0 | 2026-02-11 16:09 | 2026-02-11 16:15 | 6 | 6 | Link went down and restored after 6 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
18 | NA | NA | 2026-02-11 | Vishnu/Amr | Node Down | Link Down | RJ45 cable was loose from switch to CCTV POE | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-11 18:31 | 2026-02-11 18:34 | 3 | 2026-02-11 19:21 | 2026-02-11 20:14 | 53 | 103 | RJ45 cable cleaned and fixed properly | Completed | Maintainer | N/a | N/a | Network Back Online
19 | NA | NA | 2026-02-12 | Vishnu/Amr | Node Down | Device Down | NA | SAL-ENC26-CE-01 |  | zone 56 | 51.2478413 25.1435454 | Outside Doha | Critical | 2026-02-12 17:16 | 2026-02-12 17:18 | 2 | 2026-02-12 17:18 | 2026-02-12 17:39 | 21 | 23 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
20 | NA | NA | 2026-02-14 | Vishnu/Amr | Node Down | Device Down | NA | SAL-ENC20-CE-01,SAL-ENC14-CE-01,SAL-ENC20-UPE-02 |  | zone 56 | 51.3063942 25.164986 | Outside Doha | Critical | 2026-02-14 16:22 | 2026-02-14 16:25 | 3 | 2026-02-14 16:25 | 2026-02-14 16:54 | 29 | 32 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
21 | Sirti-WAN-R3-Ticket-01 | NA | 2026-02-15 | Vishnu/Amr | Node Down | Device Down | FLM visited the site and found no kahramaa power in cabinet as well as FP | P028C2-ENC18-CE-01,P028C2-ENC25-CE-01,P028C2-ENC25-UPE-01 |  | Zone 18 | 25.28983, 51.51513 | Inside Doha | Critical | 2026-02-15 07:13 | 2026-02-15 07:15 | 2 | 2026-02-15 07:20 | 2026-02-15 08:48 | 88 | 95 | FLM Team contacted kharamaa and they restored the power | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
22 | Sirti-WAN-R3-Ticket-02 | NA | 2026-02-15 | Vishnu/Amr | Node Down | Device Down | FLM visited the site and found no kahramaa power in cabinet as well as FP | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-15 07:44 | 2026-02-15 07:46 | 2 | 2026-02-15 08:31 | 2026-02-15 12:06 | 215 | 262 | Power restored by kharamaa team raised a ticket.Ref No-261100006258 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
23 | Sirti-WAN-R3-Ticket-03 | NA | 2026-02-15 | Saleem/Amr | Node Down | Link Down | FLM visited the site and found port 05 down which is connected to LAN access switch | 22FEB-ENC25-CE-01 |  | Zone 34 | 51.47088144, 25.31832397 | Inside Doha | Critical | 2026-02-15 11:38 | 2026-02-15 11:47 | 9 | 2026-02-15 11:47 | 2026-02-15 13:08 | 81 | 90 | The Alarm was cleared after LAN device came up | Completed | Maintainer | N/a | N/a | Network Back Online
24 | Sirti-WAN-R3-Ticket-04 | NA | 2026-02-16 | Amr | Node Down | Device Down | NA | P010-ENC61-CE-01,P010-ENC64-CE-01 |  | - | 51.4699752 25.1700975 | - | Critical | 2026-02-16 09:23 | 2026-02-16 09:24 | 1 | 2026-02-16 09:24 | 2026-02-16 09:40 | 16 | 17 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
25 | Sirti-WAN-R3-Ticket-05 | NA | 2026-02-17 | Vishnu/Haroon | No Power Redeundancy | Power Module Power off | MCB was tripped at SMDB | P012-ENC97-UPE-02 |  | Zone 56 | 25.1926322 51.4542203 | Outside Doha | Critical | 2026-02-17 16:37 | 2026-02-17 16:41 | 4 | 2026-02-17 17:02 | 2026-02-17 22:36 | 334 | 359 | FLM Turned on the CB and device restored | Completed | Non-maintainer | Access | Got the key from the Tunnel contractor and turned on the CB | Network Back Online
26 | Sirti-WAN-R3-Ticket-06 | NA | 2026-02-20 | Aneesh/Abubaker | Node Down | Device Down | P023C2-ENC16-CE-01 & P023C2-ENC16-UPE-02 unreachable from eSite | P023C2-ENC16-CE-01 & P023C2-ENC16-UPE-02 |  | Zone 82 | 25.228079 51.307359 | Outside Doha | Critical | 2026-02-20 04:33 | 2026-02-20 04:42 | 9 | 2026-02-20 06:50 | 2026-02-20 07:10 | 20 | 157 | FLM Turned on the CB and devices restored | Completed | Maintainer | N/a | N/a | Network Back Online
27 | Sirti-WAN-R3-Ticket-07 | NA | 2026-02-20 | Mastan/Adil | Node Down | Device Down | Port Down at CE Connected to Lan 2 Switch | SAL-ENC20-CE-01 |  | - | - | - | Critical | 2026-02-20 08:48 | 2026-02-20 09:00 | 12 | 2026-02-20 09:00 | 2026-02-20 09:04 | 4 | 16 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
28 | Sirti-WAN-R3-Ticket-08 | NA | 2026-02-21 | Haroon/Masthan | Ethernet link down | Link Down | Eth link down RMC-P003 &SOC-P003 &P004-SOC PRI due QNBN activity on the link | RMC-P003 &SOC-P003 &P004-SOC PRI | - | - | - | - | Critical | 2026-02-21 12:21 | 2026-02-21 12:24 | 3 | 2026-02-21 12:24 | 2026-02-21 16:26 | 242 | 245 | Activity was finished and link was restored | Completed | Non-maintainer | 3rd Party | QNBN activity on the link | Network Back Online
29 | Sirti-WAN-R3-Ticket-09 | NA | 2026-02-22 | AMR / Vishnu | Device Down | Device Down | NA | P028C2-ENC04-CE-01-OMC LOCAL | - | - | - | - | Critical | 2026-02-22 10:32 | 2026-02-22 10:35 | 2.8333 | 2026-02-22 10:35 | 2026-02-22 10:44 | 9 | 11.8333 | Alarm Auto Cleared before flm visit the site | Completed | Maintainer | N/a | N/a | Network Back Online
30 | Sirti-WAN-R3-Ticket-10 | NA | 2026-02-22 | AMR / Erick | Link Down | Link Down | TTG team was working at RMC Datacenter on RMC-ENC-NMS-SW-01 SERVER as a part of snag clearanace | RMC-ENC-NMS-SW-01 SERVER | - | - | - | - | Critical | 2026-02-22 11:52 | 2026-02-22 11:53 | 1 | 2026-02-22 11:52 | 2026-02-22 12:03 | 11.25 | 11.25 | Alarm Auto Cleared | Completed | Non-maintainer | 3rd Party | TTG team was working at RMC Datacenter | Network Back Online
31 | Sirti-WAN-R3-Ticket-11 | NA | 2026-02-22 | AMR / Haroon / Erick | Port Module Offline | One Power Source is Down | Power cable loose between DWDM and PDU | RAA_SEC | - | Zone 28 | 25.285228, 51.551657 | Inside Doha | Critical | 2026-02-22 10:54 | 2026-02-22 10:54 | 0 | 2026-02-22 10:54 | 2026-02-22 15:24 | 269 | 269 | FLM Visit the site and found the low voltage and fix the power source | Completed | Maintainer | N/a | N/a | Network Back Online
32 | Sirti-WAN-R3-Ticket-12 | NA | 2026-02-23 | HAROON | High Temprature | LPU Board 2 | Boards Temprature higher than the upper threshold | P060-ENC18-UPE-01 | - | - | - | - | Critical | 2026-02-23 14:28 | 2026-02-23 14:30 | 2 | 2026-02-23 14:30 | 2026-02-23 14:38 | 8 | 10 | Alarm Auto Cleared before flm visit the site | Completed | Maintainer | N/a | N/a | Network Back Online
33 | Sirti-WAN-R3-Ticket-13 | NA | 2026-02-24 | Adel / Umair | Device Down | Device Down | Breaker off from the FP side | P023C3-ENC174-UPE02 & P023C3-ENC174-CE 01 | - | Zone 94 | 25.01688 51.49047 | Outside Doha | Critical | 2026-02-24 03:48 | 2026-02-24 03:52 | 5 | 2026-02-24 05:01 | 2026-02-24 05:20 | 19.5 | 92.5 | MCB was tripped , FLM switched on the MCB | Completed | Maintainer | N/a | N/a | Network Back Online
34 | Sirti-WAN-R3-Ticket-14 | NA | 2026-02-24 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | NA | DUK-ENC04-CE-01 | - | - | - | - | Critical | 2026-02-24 10:23 | 2026-02-24 10:29 | 6 | 2026-02-24 10:29 | 2026-02-24 10:46 | 16.2833 | 22.2833 | Alarm Auto Cleared | Completed | Maintainer | N/a | N/a | Network Back Online
35 | Sirti-WAN-R3-Ticket-15 | NA | 2026-02-24 | AMR | Link Down | Link Down | NA | DUK-ENC06-CE-01 | - | - | - | - | Critical | 2026-02-24 11:47 | 2026-02-24 11:47 | 0 | 2026-02-24 11:47 | 2026-02-24 12:12 | 24.7333 | 24.7333 | Alarm Auto Cleared | Completed | Maintainer | N/a | N/a | Network Back Online
36 | Sirti-WAN-R3-Ticket-16 | NA | 2026-02-24 | HAROON\Masthan | High Temprature | LPU Board 2 Heatup | Boards Temprature higher than the upper threshold | P060-ENC18-UPE-01 | - | Zone 70 | 25.388045, 51.488990 | Outside Doha | Critical | 2026-02-24 13:09 | 2026-02-24 13:10 | 1 | 2026-02-24 13:30 | 2026-02-24 15:21 | 111 | 132 | FLM Visit the site and Turn on the AC Breaker and restore the Cooling | Completed | Maintainer | N/a | N/a | Network Back Online
37 | Sirti-WAN-R3-Ticket-17 | NA | 2026-02-25 | AMR / Vishnu | Communication betweeen NMS and NE is Abnormal | Device Down / Link Down | There was no power supply in main terminals of DGME-23 | P059-C1-ENC23-CE-01 P059-C1-ENC23-UPE-02 P059-C1-ENC04-UPE-01 P059-C1-ENC42-CE-01 | - | Zone 71 | 25.451633, 51.409080 | Outside Doha | Critical | 2026-02-25 08:13 | 2026-02-25 08:14 | 1 | 2026-02-25 08:57 | 2026-02-25 10:20 | 83.25 | 127.25 | Switched the Circuit from Primary to Secondary in ATS at Feeder side(ITS FP-16) | Completed | Maintainer | N/a | N/a | Network Back Online
38 | Sirti-WAN-R3-Ticket-18 | NA | 2026-02-26 | AMR / Vishnu | Link Down | Link Down | Other Ashghal Contractor (ITS Qatar) was doing the maintenance for PTZ Camera)-On NMS port down GE1/0/15 -Huawei Switch | DUK-ENC12-CE-01 | - | Zone 80 | 25.430216, 51.149749 | Outside Doha | Critical | 2026-02-26 08:04 | 2026-02-26 08:06 | 2 | 2026-02-26 08:04 | 2026-02-26 08:42 | 37.7667 | 37.7667 | FME arrived at the site and found that ITS Qatar was performing maintenance on the PTZ camera. After the maintenance was completed, the alarm was cleared-Verified the ports in Huawei Switch, all were working well | Completed | Non-maintainer | 3rd Party | ITS Qatar was performing maintenance | Network Back Online
39 | Sirti-WAN-R3-Ticket-19 | NA | 2026-02-26 | AMR / Vishnu | Link Down | Link Down | NA -On NMS port down GE1/0/15 -Huawei Switch | SAL-ENC45-CE-01 | - | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-26 08:24 | 2026-02-26 08:26 | 2 | 2026-02-26 08:26 | 2026-02-26 08:47 | 21 | 23 | FME arrived Verified the ports in Huawei Switch, all were working well- Link went down and restored after 22 min 49 sec | Completed | Maintainer | N/a | N/a | Network Back Online
40 | Sirti-WAN-R3-Ticket-20 | NA | 2026-02-26 | AMR / Vishnu | Link Down | Link Down | NA -On NMS port down GE1/0/9 -Huawei Switch | DUK-ENC16-CE-01 | - | Zone 80 | 25.432295, 51.110656 | Outside Doha | Critical | 2026-02-26 09:02 | 2026-02-26 09:04 | 2 | 2026-02-26 09:11 | 2026-02-26 09:25 | 14 | 23 | FME arrived Verified the ports in Huawei Switch, all were working well- Link went down and restored | Completed | Maintainer | N/a | N/a | Network Back Online
41 | Sirti-WAN-R3-Ticket-21 | NA | 2026-02-26 | AMR / Vishnu | Link Down | Link Down | NA -On NMS port down GE1/0/10 -Huawei Switch | SAL-ENC50-CE-01 | - | Zone 96 | 24.951308, 50.999354 | Outside Doha | Critical | 2026-02-26 10:21 | 2026-02-26 10:21 | 0 | 2026-02-26 10:29 | 2026-02-26 10:45 | 16 | 24 | FME arrived Verified the ports in Huawei Switch, all were working well- Link went down and restored | Completed | Maintainer | N/a | N/a | Network Back Online
42 | Sirti-WAN-R3-Ticket-22 | NA | 2026-02-26 | AMR / Vishnu | Communication betweeen NMS and NE is Abnormal | Communication betweeen NMS and NE is Abnormal | Issue Esclated to Imran (SALAM TECH) by call and whats app messages | P008-C3-ENC19-CE-01 P008-C3-ENC09-CE-01 P008-C3-ENC05-CE-01 P008-C3-ENC07-CE-01 P008-C3-ENC04-CE-01 P008-C3-ENC01-CE-01 | - | - | - | - | Critical | 2026-02-26 10:31 | 2026-02-26 10:31 | 0 | 2026-02-26 10:31 | 2026-02-26 11:35 | 64.1833 | 64.1833 | Issue Esclated to Imran (SALAM TECH) by call and whats app messages - All alarms got cleared | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
43 | Sirti-WAN-R3-Ticket-23 | NA | 2026-02-27 | HAROON / Patric | Heat Alarm | SFP Interface Heat Alarm | Optical Module temp too high | P010-ENC01-CE-01 | - | Zone 81 | 25.139881, 51.407393 | Outside Doha | Critical | 2026-02-27 12:08 | 2026-02-27 12:11 | 3 | 2026-02-27 12:11 | 2026-02-27 15:35 | 204 | 207 | Alarm is about SFP interface heatup overall device stats are normal, no Service Effected.alarms got cleared | Completed | Maintainer | N/a | N/a | Network Back Online
44 | Sirti-WAN-R3-Ticket-24 | NA | 2026-02-28 | AMR | Link Down | Link Down | NA | SAL-ENC67-CE-01 | - | - | - | - | Critical | 2026-02-28 11:06 | 2026-02-28 11:06 | 0 | 2026-02-28 11:06 | 2026-02-28 11:23 | 17.05 | 17.05 | Link went down and restored Auto | Completed | Maintainer | N/a | N/a | Network Back Online
45 | Sirti-WAN-R3-Ticket-25 | NA | 2026-03-03 | AMR | Link Down | Link Down | NA | DUK-ENC34-CE-01 | - | Zone 72 | 25.4537767 50.8835078 | Outside Doha | Critical | 2026-03-03 12:18 | 2026-03-03 12:18 | 0 | 2026-03-03 12:18 | 2026-03-03 12:45 | 27.05 | 27.05 | Issue esclated to RMC team and they have update Team is doing PM for End device | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
46 | Sirti-WAN-R3-Ticket-26 | NA | 2026-03-04 | AMR | PWR Module Stopped Working | Power Module Power off | PDU Was OFF | RAA-TCR-USG-02 / DWDM RAA_SEC | - | Zone 18 | 25.28522778 51.55165688 | Inside Doha | Critical | 2026-03-04 08:22 | 2026-03-04 08:24 | 2 | 2026-03-04 09:00 | 2026-03-04 09:36 | 36.7667 | 74.7667 | FLM Turned on the CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online
47 | Sirti-WAN-R3-Ticket-27 | NA | 2026-03-04 | AMR | ASH_WDM_RAA-P015-OSC_Protection ASH_WDM_RAA-P012-OSC_Protection ASH_WDM_SOC-P012-OCH-CH-54_Protection_L ASH_WDM_RMC-P012-OCH-CH-56_Protection_L ASH_WDM_SOC-P015-OCH-CH-58_Protection_S ASH_WDM_RMC-P015-OCH-CH-60_Protection_L | RAA_Sec Subrack 2 was down due to power issue | PWR cable at PDU side was loose | DWDM RAA_SEC | - | Zone 18 | 25.28522778 51.55165688 | Inside Doha | Critical | 2026-03-04 09:20 | 2026-03-04 09:20 | 0 | 2026-03-04 09:41 | 2026-03-04 09:52 | 11.7833 | 32.7833 | FLM fixed the loose power cable connection by cable tie /to be plan for PDU replacement | Completed | Maintainer | N/a | N/a | Network Back Online
48 | Sirti-WAN-R3-Ticket-28 | NA | 2026-03-08 | Abubaker | Power Module Powered off | Power Module Power off | khahromaa power shutdown | - P004-TMC-NPE-01 - P004_Pri - P004_Sec | - | - | 25.319385,51.352255 | Outside Doha | Critical | 2026-03-08 05:23 | 2026-03-08 05:28 | 5.4833 | 2026-03-08 06:01 | 2026-03-08 07:01 | 60.8333 | 98.8333 | Main Power was down due to power outage from KAHRAMAA side, Alarms cleared after KAHRAMAA power recovered by KAHRAMAA team | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
49 | Sirti-WAN-R3-Ticket-29 | NA | 2026-03-08 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no PWR at ENC / FP CB was tripped | P004-ENC43-UPE-02 P004-ENC43-CE-01 P023C2-ENC43-CE-01 | - | - |  |  | Critical | 2026-03-08 17:23 | 2026-03-08 17:27 | 4 | 2026-03-08 18:02 | 2026-03-08 18:19 | 16.5 | 55.5 | The FME team reached the site and found that there was no power in the ENC cabinet. Upon checking the FP cabinet, they found that the main circuit breaker (CB) was in the OFF (tripped) state. The CB was switched ON, after which all devices were restored and the alarms were cleared | Completed | Maintainer | N/a | N/a | Network Back Online
50 | Sirti-WAN-R3-Ticket-30 | NA | 2026-03-09 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-09 08:00 | 2026-03-09 08:06 | 6.25 | 2026-03-09 09:02 | 2026-03-09 09:45 | 43.5167 | 105.5167 | there was no UPS output power , FLM Turned on the UPS | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
51 | Sirti-WAN-R3-Ticket-31 | NA | 2026-03-09 | Adel | power module stopped working , power fail | power fail | alarm is auto clear before visiting the site | P004-TMC-NPE-01 P004-sec P004-pri | - | - | 25.319385 ,51.352255 | Outside Doha | Critical | 2026-03-09 10:14 | 2026-03-09 10:17 | 3.1833 | 2026-03-09 10:17 | 2026-03-09 10:29 | 12.3333 | 15.5167 | alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
52 | Sirti-WAN-R3-Ticket-32 | NA | 2026-03-09 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-09 10:36 | 2026-03-09 10:40 | 4.2667 | 2026-03-09 11:03 | 2026-03-09 11:14 | 10.9667 | 37.9667 | there was no UPS output power , FLM Turned on the UPS | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
53 | Sirti-WAN-R3-Ticket-33 | NA | 2026-03-09 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-09 12:14 | 2026-03-09 12:18 | 4 | 2026-03-09 13:04 | 2026-03-09 13:26 | 21.9 | 71.9 | there was no UPS output power , FLM Turned on the UPS, disconnected the AC from the UPS | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
54 | Sirti-WAN-R3-Ticket-34 | NA | 2026-03-09 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | NA | P010-ENC61-CE-01 | - | - | - | - | Critical | 2026-03-09 15:38 | 2026-03-09 15:38 | 0 | 2026-03-09 15:38 | 2026-03-09 15:49 | 10.9167 | 10.9167 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
55 | Sirti-WAN-R3-Ticket-35 | NA | 2026-03-10 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | tripped CB | P029C2-ENC05-CE-01 | - | - | 25.281278° ,51.503972° | Inside Doha | Critical | 2026-03-10 07:33 | 2026-03-10 07:36 | 2.9 | 2026-03-10 08:20 | 2026-03-10 09:13 | 52.7667 | 99.7667 | FLM switched on tripped CB | Completed | Maintainer | N/a | N/a | Network Back Online
56 | Sirti-WAN-R3-Ticket-36 | NA | 2026-03-10 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | alarm is auto clear before visiting the site | SAL-ENC63-CE-01 | - | - | 24.8301249° ,50.8705931° | Outside Doha | Critical | 2026-03-10 12:15 | 2026-03-10 12:18 | 3.3167 | 2026-03-10 12:18 | 2026-03-10 13:12 | 54.3667 | 57.6833 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
57 | Sirti-WAN-R3-Ticket-37 | NA | 2026-03-11 | Aaqib | VRRP switchover performed | VRRP switchover performed | Alarm auto cleared. Suspecting link fluctuation | P023C2-Enc11-CE-01 | - | - | 25.325262° , 51.329176° | Outside Doha | Critical | 2026-11-03 04:02 | 2026-11-03 04:04 | 2.0333 | 2026-11-03 04:04 | 2026-11-03 04:06 | 2 | 4.0333 | Alarm auto cleared | Completed | Maintainer | N/a | N/a | Network Back Online
58 | Sirti-WAN-R3-Ticket-38 | NA | 2026-03-11 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-11 07:28 | 2026-03-11 07:34 | 6 | 2026-03-11 08:38 | 2026-03-11 09:50 | 71.95 | 141.95 | FLM disconnected the AC from UPS and connected it directly to CB | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
59 | Sirti-WAN-R3-Ticket-39 | NA | 2026-03-11 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | No power in cabinet | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-11 15:02 | 2026-03-11 15:05 | 3 | 2026-03-11 15:43 | 2026-03-11 16:14 | 30.6 | 71.6 | FLM disconnected the AC from UPS and connected it directly to CB , team is monitoring the UPS behavior after the action | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
60 | Sirti-WAN-R3-Ticket-40 | NA | 2026-03-12 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | DEVICE DOWN DUE TO UPS FAULTY | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-12 09:19 | 2026-03-12 09:21 | 2 | 2026-03-12 09:57 | 2026-03-12 10:50 | 53.2667 | 91.2667 | UPS FAULTY need to replace .for now remove the UPS connetion temporary now we directly connect the device | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
61 | Sirti-WAN-R3-Ticket-41 | NA | 2026-03-12 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | NA | SAL-ENC56-CE-01 | - | - | 24.891173, 50.938318 | - | Critical | 2026-03-12 10:52 | 2026-03-12 10:53 | 1 | 2026-03-12 10:53 | 2026-03-12 11:38 | 45.1167 | 46.1167 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
62 | Sirti-WAN-R3-Ticket-42 | NA | 2026-03-13 | AMR | Link Down | Link Down | Cable Loose | P008C2-ENC01-CE-01 | - | - | 25.236901, 51.521726 | - | Critical | 2026-03-13 10:52 | 2026-03-13 10:57 | 5 | 2026-03-13 11:00 | 2026-03-13 11:11 | 11.6167 | 19.6167 | FME clean the cable and fix it properly | Completed | Maintainer | N/a | N/a | Network Back Online
63 | Sirti-WAN-R3-Ticket-43 | NA | 2026-03-15 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | As per Logs, there was power interruption at site | P011-Enc26-UPE-01 P011-Enc26-CE-01 | - | - | 25.22234, 51.542 | - | Critical | 2026-03-15 03:25 | 2026-03-15 03:26 | 1 | 2026-03-15 03:26 | 2026-03-15 03:31 | 5 | 6 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Devices Back Online
64 | Sirti-WAN-R3-Ticket-44 | NA | 2026-03-17 | AMR | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet | SAL-ENC14-CE-01 | - | - | 25.1858801° 51.3628538° | - | Critical | 2026-03-17 09:59 | 2026-03-17 10:01 | 2 | 2026-03-17 10:01 | 2026-03-17 10:49 | 47.2833 | 49.2833 | The Kahramaa team was working at FP. Once they completed their work and cable termination, power was restored, all devices came up, and all alarms were cleared. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
65 | Sirti-WAN-R3-Ticket-45 | NA | 2026-03-18 | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | As per Logs, there was power interruption at site | P006-ENC02-CE-01 | - | - | 25.2190399° 51.4369501° | - | Critical | 2026-03-18 09:59 | 2026-03-18 10:05 | 5.3167 | 2026-03-18 10:05 | 2026-03-18 10:10 | 5 | 10.3167 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
66 | Sirti-WAN-R3-Ticket-46 | NA | 2026-03-19 | Abubaker | Optical Model temperature too high | SFP Alarm | Alarm cleared automatically by itself after 1h & 11mins | P010-ENC01-CE-01 | - | - | 25.1398815, 51.4073931 | Outside Doha | Critical | 2026-03-19 14:58 | 2026-03-19 14:59 | 1.4833 | 2026-03-19 15:21 | 2026-03-19 16:09 | 48.3 | 71.7833 | Alarm auto cleared | Completed | Maintainer | N/a | N/a | Devices Back Online
67 | Sirti-WAN-R3-Ticket-47 | NA | 2026-03-20 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet due to the failure of SLFP cabient which is uder RF001 | P003-ENC10-CE-DGME-01 | - | - | 25.3735283 51.5285481 | Inside Doha | Critical | 2026-03-20 09:08 | 2026-03-20 09:12 | 3.1167 | 2026-03-20 09:31 | 2026-03-20 13:49 | 257.95 | 280.0667 | Sirti MENAA has communicated RMC to request RF001 to fix SLFP Panel, after they rectify the panel, the power back to ITS-FP and all nodes back online | Completed | Non-maintainer | 3rd Party | RF001 | Network Back Online
68 | Sirti-WAN-R3-Ticket-48 | NA | 2026-03-21 | Aaqib/Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet due to the failure of SLFP cabient which is uder RF001 | P003-Enc10-CE-DGME-01 | - | - | 25.3735283 51.5285481 | Inside Doha | Critical | 2026-03-21 07:42 | 2026-03-21 07:46 | 3.8 | 2026-03-21 08:25 | 2026-03-21 18:01 | 575.3667 | 618.8167 | Sirti MENAA has communicated RMC to request RF001 to fix SLFP Panel, after they rectify the panel, the power back to ITS-FP and all nodes back online | Completed | Non-maintainer | 3rd Party | RF001 | Network Back Online
69 | Sirti-WAN-R3-Ticket-49 | NA | 2026-03-21 | Aaqib | Link Down | Link down | Link down towards LAN | Sal-Enc45-CE-01 |  |  |  | Outside Doha | Low | 2026-03-21 12:59 | 2026-03-21 12:59 | 0 | 2026-03-21 12:59 | 2026-03-21 13:05 | 6.05 | 6.05 | Link auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
70 | Sirti-WAN-R3-Ticket-50 | NA | 2026-03-21 | Sanket | Link Down | LAN Link down | Link down towards LAN | SAL-ENC14-CE-01 |  |  |  | Outside Doha | Low | 2026-03-21 19:26 | 2026-03-21 19:26 | 0 | 2026-03-21 19:26 | 2026-03-21 19:30 | 3.9167 | 3.9167 | Link auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
71 | Sirti-WAN-R3-Ticket-51 | NA | 2026-03-21 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet. | P003-ENC10-CE-DGME-01 |  |  | 25.3735283 51.5285481 | Outside Doha | Critical | 2026-03-21 20:41 | 2026-03-21 20:43 | 2 | 2026-03-21 20:52 | 2026-03-21 20:57 | 4.35 | 15.3 | Temperory generator removed and supply given from Kharamaa. | Completed | Non-maintainer | N/a | State Kahramaa | Network Back Online
72 | Sirti-WAN-R3-Ticket-52 | NA | 2026-03-21 | Sanket | Link Down | LAN Link down | Link down towards LAN | SAL-ENC20-CE-01 |  |  |  | Outside Doha | Low | 2026-03-21 20:52 | 2026-03-21 20:52 | 0 | 2026-03-21 20:53 | 2026-03-21 21:00 | 7.0833 | 8.0833 | Link auto restored. The link is down towards LAN | Completed | Maintainer | N/a | N/a | Network Back Online
73 | Sirti-WAN-R3-Ticket-53 | NA | 2026-03-21 | Sanket/Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | There was no power on the outgoing-1 of the PSU | P003-ENC37-CE-DGME-01 | - | - | 25.3364931° 51.51767° | Inside Doha | Critical | 2026-03-21 21:33 | 2026-03-21 21:36 | 3.4167 | 2026-03-21 23:00 | 2026-03-21 23:32 | 31.8 | 119.3333 | We checked outgoing-2, and it's found sufficient, we connect the switch to outgoing-2 of PSU | Completed | Maintainer | N/a | N/a | Network Back Online
74 | Sirti-WAN-R3-Ticket-54 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Device Restored before team visit | IE-5000-1003.ASHGAL | - | - | - | Inside Doha | Critical | 2026-03-23 01:24 | 2026-03-23 01:31 | 7.25 | 2026-03-23 01:24 | 2026-03-23 05:39 | 255.1333 | 255.1333 | that switch is LAN switch managed by WAN NMS , team doesnot have the location of the switch and that escalated to 3rd party , at time 5:38 am the devices come back online without visiting | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
75 | Sirti-WAN-R3-Ticket-55 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found MCB was tripped | P017C2-ENC23-CE01 | - | - | 25.1702778° 51.4710278° | Inside Doha | Critical | 2026-03-23 02:11 | 2026-03-23 02:17 | 6.3 | 2026-03-23 04:23 | 2026-03-23 04:28 | 4.6167 | 137.0833 | FLM switched on cabinet main CB , tripped due to rain | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
76 | Sirti-WAN-R3-Ticket-56 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no kharama power on site. | DUK-ENC30-CE01 | - | - | 25.4637854° 50.930279° | Outside Doha | Critical | 2026-03-23 02:11 | 2026-03-23 02:14 | 2.8167 | 2026-03-23 02:39 | 2026-03-23 08:53 | 374.0333 | 402.0333 | FLM visit the site and found that no kharama power on site. Ticket (Ref # 261100010894) is raised with kahrama. Device restored after kahahrama power restoration | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
77 | Sirti-WAN-R3-Ticket-57 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | cabinet main CB is off | P008C2-ENC01-CE-01 | - | - | 25.2369009° 51.521726° | Inside Doha | Critical | 2026-03-23 02:23 | 2026-03-23 02:26 | 3.4 | 2026-03-23 02:36 | 2026-03-23 04:23 | 107.8 | 120.8 | FLM switched on cabinet main CB , tripped due to rain | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
78 | Sirti-WAN-R3-Ticket-58 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Main UPS CB is tripped | P007C2-ENC82-CE-01 | - | - | 25.3045066° 51.4548113° | Inside Doha | Critical | 2026-03-23 02:39 | 2026-03-23 02:49 | 9.8667 | 2026-03-23 05:49 | 2026-03-23 05:55 | 6.5167 | 196.0833 | FLM switched on main UPS CB | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
79 | Sirti-WAN-R3-Ticket-59 | NA | 2026-03-23 | Adel | Power Module stopped working | Power Module stopped working | Team found the CB powering up Source B is faulty | P015-ENC19A-CE-01 | - | - | 25.1328013° 51.5759416° | Inside Doha | Critical | 2026-03-23 02:47 | 2026-03-23 02:52 | 4.6333 | 2026-03-23 03:12 | 2026-03-23 07:50 | 277.6833 | 302.6833 | The main CB has been replaced | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
80 | Sirti-WAN-R3-Ticket-60 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found that CB was tripped | P007C2-ENC99-UPE02 P007C2-ENC99-CE01 | - | - | 25.2967109° 51.4488814° | Inside Doha | Critical | 2026-03-23 06:17 | 2026-03-23 06:20 | 2.7667 | 2026-03-23 07:03 | 2026-03-23 07:18 | 15.4333 | 60.9333 | FLM visit the site and was found that CB was tripped. Devices restored after turning ON CB | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
81 | Sirti-WAN-R3-Ticket-61 | NA | 2026-03-23 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | CRR-ENC02-CE-01 | - | - | 25.2834083°, 51.5496912° | Inside Doha | Critical | 2026-03-23 09:09 | 2026-03-23 09:12 | 2.7333 | 2026-03-23 09:12 | 2026-03-23 09:14 | 2.35 | 5.0833 | As per log, there was khahrama interruption at site. | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
82 | Sirti-WAN-R3-Ticket-62 | NA | 2026-03-23 | Sanket | Link Down | LAN Link down | port error disable GE 1/13 | P042-ENC08-CE-01 | - | - | - | Inside Doha | Low | 2026-03-23 17:11 | 2026-03-23 17:13 | 2.3167 | 2026-03-23 17:13 | 2026-03-23 17:19 | 5.5833 | 7.9 | The port is in error disable. After shut and unshut the port link became normal. The link is down towards LAN | Completed | Maintainer | N/a | N/a | Network Back Online
83 | Sirti-WAN-R3-Ticket-63 | NA | 2026-03-23 | Sanket | Link Down | LAN Link down | The link is down towards the LAN ( D-NODE-28 is down) | DUK-ENC30-CE01 | - | - | 25°27'16.48 50°57'15.07 | Outside Doha | Medium | 2026-03-23 17:46 | 2026-03-23 17:51 | 5 | 2026-03-23 18:33 | 2026-03-23 20:51 | 138.4333 | 185.2333 | As per LAN team, D-Node 28 is down and No Kharamaa power available in the cabinet. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
84 | Sirti-WAN-R3-Ticket-64 | NA | 2026-03-23 | Sanket | Link Down | LAN Link down | Link down towards LAN | SAL-ENC32-CE-01 | - | - | 25.1165799° 51.1812367° | Outside Doha | Low | 2026-03-23 19:39 | 2026-03-23 19:41 | 2.8167 | 2026-03-23 19:41 | 2026-03-23 19:45 | 3.35 | 6.1667 | Link auto restored. The link is down towards LAN | Completed | Maintainer | N/a | N/a | Network Back Online
85 | Sirti-WAN-R3-Ticket-65 | NA | 2026-03-23 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | IE5000-2302 | - | - | - | Outside Doha | Critical | 2026-03-23 22:19 | 2026-03-23 22:21 | 2 | 2026-03-23 22:21 | 2026-03-23 22:22 | 1.2 | 3.2 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
86 | Sirti-WAN-R3-Ticket-66 | NA | 2026-03-24 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | No power in 1 phase of Khahrama | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-24 01:11 | 2026-03-24 01:17 | 5.5833 | 2026-03-24 02:06 | 2026-03-24 03:20 | 74.65 | 129 | - The node was down due to unavailability of the power in 2 phases. - KAHRAMAA Service Request raised. - As a WA, the node connected to the phase line having power. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
87 | Sirti-WAN-R3-Ticket-67 | NA | 2026-03-24 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Team found that CB was tripped | SAL-ENC50-CE-01 | - | - | 24.9513076° 50.9993542° | Outside Doha | Critical | 2026-03-24 09:46 | 2026-03-24 09:49 | 3.2167 | 2026-03-24 09:54 | 2026-03-24 10:48 | 53.4667 | 61.85 | FLM visit the site and found MCB at FP was tripped. Device restored after switching ON MCB at FP. | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
88 | Sirti-WAN-R3-Ticket-68 | NA | 2026-03-24 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Team found that CB was tripped | P003-ENC10-CE-DGME-01 | - | - | 25.3735283 51.5285481 | Outside Doha | Critical | 2026-03-24 10:31 | 2026-03-24 10:33 | 2.0667 | 2026-03-24 11:45 | 2026-03-24 12:21 | 36.5833 | 109.9667 | FLM visit the site and found MCB at FP was tripped. Device restored after switching ON MCB at FP. | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
89 | Sirti-WAN-R3-Ticket-69 | NA | 2026-03-24 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | Team found that CB was tripped | P007C7P1-ENC01-CE-01 | - | - | 25.339487° 51.4610983° | Inside Doha | Critical | 2026-03-24 12:04 | 2026-03-24 12:06 | 2 | 2026-03-24 12:21 | 2026-03-24 15:51 | 210.3333 | 227.3333 | As per Slam Tech team, CB was tripped. Devices restored after turning ON CB | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
90 | Sirti-WAN-R3-Ticket-70 | NA | 2026-03-24 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | DUK-ENC06-CE-01 | - | - | 25.3954062° 51.1985851° | Outside Doha | Critical | 2026-03-24 13:38 | 2026-03-24 13:46 | 8.1667 | 2026-03-24 13:46 | 2026-03-24 13:59 | 13.0333 | 21.2 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
91 | Sirti-WAN-R3-Ticket-71 | NA | 2026-03-25 | Abubaker | Link Down | LAN Link down | The cable toward the CCTV is disconnected (GE 1/0/10) | SAL-ENC50-CE-01 | - | - | 24.9513076, 50.9993542 | Outside Doha | Critical | 2026-03-24 23:19 | 2026-03-24 23:27 | 7.8 | 2026-03-25 00:25 | 2026-03-25 01:20 | 55.05 | 120.85 | 3rd Party ccntractor ITSQ change the RJ45 connector at POE end and Port is up | Completed | Non-maintainer | 3rd Party | 3rd Party ccntractor | Port is up and alarm cleared | Khadar basha syed
92 | Sirti-WAN-R3-Ticket-72 | NA | 2026-03-25 | Abubaker | Link Down | LAN Link down | RJ45 Connector was found faulty | SAL-ENC50-CE-01 | - | - | 24.9513076, 50.9993542 | Outside Doha | Critical | 2026-03-25 02:42 | 2026-03-25 02:48 | 5.8833 | 2026-03-25 02:48 | 2026-03-25 03:01 | 12.6667 | 18.55 | Auto clear before team visit | Completed | Maintainer | N/a | N/a | Port is up and alarm cleared
93 | Sirti-WAN-R3-Ticket-73 | NA | 2026-03-25 | Abubaker | Link Down | LAN Link down | Short Circuit in 3 Phase khahrama connection | DUK-ENC12-CE-01 | - | - | 25.4322949° 51.1106559° | Outside Doha | Critical | 2026-03-25 03:53 | 2026-03-25 03:56 | 2.9667 | 2026-03-25 04:46 | 2026-03-25 06:24 | 97.3667 | 150.3167 | The cabinet power issue was caused by a short circuit between R/Y/B phases and Neutral in the power cable of Khahrama | Completed | Maintainer | N/a | N/a | Network Back Online | Umair Rahman
94 | Sirti-WAN-R3-Ticket-74 | NA | 2026-03-25 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB was found faulty | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-25 08:20 | 2026-03-25 08:24 | 4.4667 | 2026-03-25 09:01 | 2026-03-25 10:00 | 58.7833 | 100.6333 | Device was down due to faulty CB. Team change CB connection with spare CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online | Kwadwo Ofosu
95 | Sirti-WAN-R3-Ticket-75 | NA | 2026-03-25 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | During PPM activity / AC compressor faulty when the team make AC CB ON - the main CB went OFF | P029C2-ENC05-CE-01 | - | - | 25.281278 51.503972 | Inside Doha | Critical | 2026-03-25 12:50 | 2026-03-25 12:51 | 1 | 2026-03-25 12:54 | 2026-03-25 12:57 | 2.1 | 6.1 | During PPM activity / AC compressor faulty when the team make AC CB ON - the main CB went OFF /team make CB ON and all alarms got cleared | Completed | Maintainer | N/a | N/a | Network Back Online | Hecham
96 | Sirti-WAN-R3-Ticket-76 | NA | 2026-03-25 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | P059C1-N2-ENC19-CE-01 | - | - | 25.43425476° 51.412436° | Inside Doha | Critical | 2026-03-25 14:18 | 2026-03-25 14:22 | 4.45 | 2026-03-25 14:22 | 2026-03-25 14:24 | 2 | 6.45 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
97 | Sirti-WAN-R3-Ticket-77 | NA | 2026-03-26 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Device Restored before team visit | IE5000-1003.ashghal | - | - | 25.30462 51.51743 | Inside Doha | Critical | 2026-03-26 06:36 | 2026-03-26 06:41 | 4.6333 | 2026-03-26 06:41 | 2026-03-26 06:58 | 16.5333 | 21.1667 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
98 | Sirti-WAN-R3-Ticket-78 | NA | 2026-03-26 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | QBC team is working at FP | SAL-ENC20-CE-01 SAL-ENC20-UPE-02 | - | - | 25.164986° 51.3063942 | Inside Doha | Critical | 2026-03-26 11:06 | 2026-03-26 11:09 | 3.1 | 2026-03-26 11:09 | 2026-03-26 11:36 | 26.8833 | 29.9833 | QBC team is working at Fidder Piller | Completed | Non-maintainer | 3rd Party | 3rd Party ccntractor | Network Back Online | Patric
99 | Sirti-WAN-R3-Ticket-79 | NA | 2026-03-26 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Sub Main CB breaker tripping along with AC CB Due to AC Defect | IE5000-1003.ashghal | - | - | 25.30462 51.51743 | Inside Doha | Critical | 2026-03-26 10:15 | 2026-03-26 10:20 | 4.7333 | 2026-03-26 10:55 | 2026-03-26 11:08 | 13.05 | 52.7833 | Sub Main CB breaker Restored | Completed | Maintainer | N/a | N/a | Network Back Online | Hichem
100 | Sirti-WAN-R3-Ticket-80 | NA | 2026-03-26 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Sub Main CB breaker tripping along with AC CB due to AC defect during PPM | IE5000-1003.ashghal | - | - | 25.30462 51.51743 | Inside Doha | Critical | 2026-03-26 12:34 | 2026-03-26 12:38 | 4 | 2026-03-26 12:38 | 2026-03-26 12:48 | 10.5 | 14.5 | Change AC Capacitor and deep cleaning of all AC components | Completed | Maintainer | N/a | N/a | Network Back Online | Hichem
101 | Sirti-WAN-R3-Ticket-81 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | alarm is auto clear before visiting the site | SAL-ENC26-CE-01 | - | - | 25.1435454° 51.2478413° | Outside Doha | Critical | 2026-03-26 17:14 | 2026-03-26 17:16 | 1.7167 | 2026-03-26 17:14 | 2026-03-26 17:17 | 2.25 | 2.25 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online | -
102 | Sirti-WAN-R3-Ticket-82 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found no power inside cabinet | DUK-ENC24-CE-01 | - | - | 25.435778° 51.0066732° | Outside Doha | Critical | 2026-03-26 16:38 | 2026-03-26 16:40 | 1.9 | 2026-03-26 17:54 | 2026-03-26 18:19 | 24.8833 | 100.7833 | FLM switched on main CB that was tripped | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | sanjeewa
103 | Sirti-WAN-R3-Ticket-83 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | No Khahroma power at cabenit | DUK-ENC20-CE-01 | - | - | 25.427405° 51.0546006° | Outside Doha | Critical | 2026-03-26 17:46 | 2026-03-26 17:49 | 2.6333 | 2026-03-26 19:33 | 2026-03-26 23:19 | 226.3667 | 333 | Esclated to KAHRAMAA & power was restored, all devices came up | Completed | Non-maintainer | Environmental & 3rd Party | Rain Event & State Kahramaa | Network Back Online | sanjeewa
104 | Sirti-WAN-R3-Ticket-84 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | main Cabinet CB was tripped | P060-ENC18-CE-GME-01 | - | - | 25.4042479° 51.4923233° | Outside Doha | Critical | 2026-03-26 17:35 | 2026-03-26 17:40 | 4.5667 | 2026-03-26 20:02 | 2026-03-26 20:16 | 13.85 | 160.4167 | FLM switched on main CB that was tripped | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | najeeb
105 | Sirti-WAN-R3-Ticket-85 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power at cabinet | SAL-ENC50-CE-01 | - | - | 24.9513076° 50.9993542° | Outside Doha | Critical | 2026-03-26 18:17 | 2026-03-26 18:18 | 1.2167 | 2026-03-26 20:49 | 2026-03-26 21:15 | 26.4667 | 178.6833 | FLM switched on main CB at feeder pillar | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | hassan
106 | Sirti-WAN-R3-Ticket-86 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power inside cabinet | SAL-ENC45-CE-01 | - | - | 25.005944° 51.042739° | Outside Doha | Critical | 2026-03-26 18:20 | 2026-03-26 18:21 | 1.2833 | 2026-03-26 19:35 | 2026-03-26 20:04 | 28.7 | 103.9833 | FLM switched on main CB at feeder pillar | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | hassan
107 | Sirti-WAN-R3-Ticket-87 | NA | 2026-03-26 | Adel | Link Down | LAN device down | No KAHRAMAA Power at the LAN device | SAL-ENC67-CE-01 | - | - | 24.7761642° 50.8665552° | Outside Doha | Critical | 2026-03-26 18:28 | 2026-03-26 18:37 | 9.0167 | 2026-03-26 19:39 | 2026-03-26 23:44 | 245.0833 | 316.1 | Esclated to KAHRAMAA & power was restored, all devices came up | Completed | Non-maintainer | Environmental & 3rd Party | Rain Event & State Kahramaa | Network Back Online | hassan
108 | Sirti-WAN-R3-Ticket-88 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power inside cabinet | P029C1-ENC02-CE-01 | - | - | 25.2779777° 51.4661648 | Inside Doha | Critical | 2026-03-26 18:48 | 2026-03-26 18:53 | 4.55 | 2026-03-26 21:31 | 2026-03-26 22:07 | 35.7 | 198.25 | FLM switched on main CB at feeder pillar & bypass the UPS as it is tripping the FB CB | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | aneesh
109 | Sirti-WAN-R3-Ticket-89 | NA | 2026-03-26 | Adel | farwarding Engine fail | device hardware fault | Everything looks normal on site | SAL-ENC32-CE-01 | - | - | 25.1165799° 51.1812367° | Outside Doha | Critical | 2026-03-26 22:15 | 2026-03-26 22:25 | 9.55 | 2026-03-26 22:18 | 2026-03-27 00:15 | 116.6667 | 119.2167 | Performed a hardware reboot for the device | Completed | Non-maintainer | Environmental | Rain Event | Alarm Cleared | aneesh