## WAN
dis saaaa | Ticket No | Maximo WO | Date | Node ID | NOC WAN Engineer | Alert Type | Issue Type | Initial Findings | Cabinet Asset Field Tag | Location | Coordinates | Area Category | Severity | Fault Notification Date and Time (dd/mm/yy hh:mm) | Fault Response Date and Time (dd/mm/yy hh:mm) | FRT Fault Response Time (Minutes) | Actual Start Date and Time (dd/mm/yy hh:mm) | Actual Finish Date and Time (dd/mm/yy hh:mm) | ART Active Repair Time (Minutes) | TRT Total Repair Time (Minutes) | Action Taken | Status | Fault Attribution | FA Class | FA (Fault Attraction) Notes | Remarks | Field Engineer
1 | NA | NA | 2026-02-01 | P010-ENC61-CE-01 | - | Communication betweeen NMS and NE is Abnormal | Device Down | FLM visited the site and confirmed that Kahramaa power was not available at the cabinet. |  | Zone 57 | 51.4699752, 25.170097 | Outside Doha | P2 - High | 2026-02-01 08:39 | 2026-02-01 08:39 | 0 | 2026-02-01 08:39 | 2026-02-01 13:57 | 318 | 318 | Power was restored by Kahramaa after 5 hours and 17 minutes.Network was up. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
2 | NA | NA | 2026-02-02 | SAL-ENC45-CE-01 | - | Link Down | Network down | Link went down |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-02-02 13:04 | 2026-02-02 13:04 | 0 | 2026-02-02 13:04 | 2026-02-02 13:08 | 4 | 4 | Link restored after 4 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
3 | NA | NA | 2026-02-02 | P008C2-Enc09-CE01 | - | Communication betweeen NMS and NE is Abnormal | Device Down | network went down due to system upgrade |  | Zone 56 | 25.253746° 51.4904411° | Outside Doha | P2 - High | 2026-02-02 06:49 | 2026-02-02 06:49 | 0 | 2026-02-02 06:49 | 2026-02-02 06:50 | 1 | 1 | Escalated to Salam Tech team (Imran) on phone and rebooted the system | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
4 | NA | NA | 2026-02-04 | Sal-ENC38-CE-01 | Vishnu | Communication betweeen NMS and NE is Abnormal | Device Down | Power failure detected at the site |  | Zone 83 | 51.1144427, 25.069908 | Outside Doha | P2 - High | 2026-02-04 07:00 | 2026-02-04 07:00 | 0 | 2026-02-04 08:00 | 2026-02-04 13:52 | 352 | 412 | The Kahramaa team is currently performing maintenance on the main electrical poles in the area.Expected Completion: Restoration is anticipated by 2:00 PM. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
5 | NA | NA | 2026-02-05 | SAL-ENC45-CE-01 | - | Link Down | Link Down | Link went down |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-02-05 12:47 | 2026-02-05 12:47 | 0 | 2026-02-05 12:47 | 2026-02-05 12:50 | 3 | 3 | Link restored after 3 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
6 | NA | NA | 2026-02-05 | SAL-ENC45-CE-01 | - | Link Down | Link Down | Link went down |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-02-05 14:25 | 2026-02-05 14:25 | 0 | 2026-02-05 14:25 | 2026-02-05 14:36 | 11 | 11 | Link restored after 11 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
7 | NA | NA | 2026-02-06 | P010-ENC61–CE-01 | Vishnu | Communication betweeen NMS and NE is Abnormal | Device Down | UPS was not giving output |  | Zone 57 | 51.4699752, 25.170097 | Outside Doha | P2 - High | 2026-02-06 09:36 | 2026-02-06 09:36 | 0 | 2026-02-06 11:01 | 2026-02-06 11:08 | 7 | 92 | Issue resolved after restarting UPS | Completed | Maintainer | N/a | N/a | Network Back Online
8 | NA | NA | 2026-02-07 | P023C1-ENC01–CE -01 | Vishnu | Communication betweeen NMS and NE is Abnormal | Device Down | Noticed no power on Main breakers/Terminals |  | Zone 91 | 51.583897, 25.111748 | Outside Doha | P2 - High | 2026-02-07 11:25 | 2026-02-07 11:25 | 0 | 2026-02-07 12:02 | 2026-02-07 13:13 | 71 | 108 | Power supply restored by Kahrama staff.Kharahma reference No. 261100005225 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
9 | NA | NA | 2026-02-07 | P023C1-ENC01–UPE -01 | Vishnu | Node DownCommunication betweeen NMS and NE is Abnormal | Device Down | Noticed no power on Main breakers/Terminals |  | Zone 91 | 51.583897, 25.111748 | Outside Doha | P2 - High | 2026-02-07 11:25 | 2026-02-07 11:25 | 0 | 2026-02-07 12:02 | 2026-02-07 13:13 | 71 | 108 | Power supply restored by Kahrama staff.Kharahma reference No. 261100005225 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
10 | NA | NA | 2026-02-08 | SAL-ENC50–CE -01 | Salem/Amr | Communication betweeen NMS and NE is Abnormal | Device Down | MCB was tripped at site |  | Zone 96 | 50.9993542, 24.9513076 | Outside Doha | P2 - High | 2026-02-08 12:29 | 2026-02-08 12:29 | 0 | 2026-02-08 13:34 | 2026-02-08 14:00 | 26 | 91 | team turned on the CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online
11 | NA | NA | 2026-02-09 | P008C3-ENC01–CE -01 | Salem/Amr | Link Down | Link Down | Link went down |  | Zone 55 | 51.4801647, 25.2614822 | Outside Doha | P3 - Medium | 2026-02-09 15:06 | 2026-02-09 15:06 | 0 | 2026-02-09 15:06 | 2026-02-09 15:08 | 2 | 2 | Escalated to Salam Tech team (Imran) on phone and rebooted the system | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
12 | NA | NA | 2026-02-09 | P008C3-ENC25–CE -01 | Salem/Amr | Link Down | Link Down | Link went down |  | Zone 56 | 51.50261, 25.2341068 | Outside Doha | P3 - Medium | 2026-02-09 15:43 | 2026-02-09 15:43 | 0 | 2026-02-09 15:43 | 2026-02-09 15:45 | 2 | 2 | Escalated to Salam Tech team (Imran) on phone and rebooted the system | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
13 | NA | NA | 2026-02-10 | P005-ENC410-CE-01 | Salem/Amr | Communication betweeen NMS and NE is Abnormal | Device Down | MCB was tripped at site |  | Zone 56 | 51.399465, 25.3102445 | Outside Doha | P2 - High | 2026-02-10 13:39 | 2026-02-10 13:39 | 0 | 2026-02-10 14:14 | 2026-02-10 15:52 | 98 | 133 | Team turned on the CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online
14 | NA | NA | 2026-02-10 | SAL-ENC45-CE-01 | Salem/Amr | Link Down | Link Down | Link went down |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-02-10 16:19 | 2026-02-10 16:19 | 0 | 2026-02-10 16:19 | 2026-02-10 16:26 | 7 | 7 | Link went down and restored after 7 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
15 | NA | NA | 2026-02-11 | SAL-ENC45-CE-01 | Salem/Amr | Link Down | Link Down | Link went down |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-02-11 12:59 | 2026-02-11 12:59 | 0 | 2026-02-11 12:59 | 2026-02-11 13:09 | 10 | 10 | Link went down and restored after 10 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
16 | NA | NA | 2026-02-11 | SAL-ENC45-CE-01 | Salem/Amr | link Down | Link Down | Link went down |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-02-11 13:10 | 2026-02-11 13:10 | 0 | 2026-02-11 13:10 | 2026-02-11 13:18 | 8 | 8 | Link went down and restored after 8 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
17 | NA | NA | 2026-02-11 | SAL-ENC45-CE-01 | Salem/Amr | Link Down | Link Down | Link went down |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-02-11 16:09 | 2026-02-11 16:09 | 0 | 2026-02-11 16:09 | 2026-02-11 16:15 | 6 | 6 | Link went down and restored after 6 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
18 | NA | NA | 2026-02-11 | SAL-ENC45-CE-01 | Vishnu/Amr | link Down | Link Down | RJ45 cable was loose from switch to CCTV POE |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-02-11 18:31 | 2026-02-11 18:34 | 3 | 2026-02-11 19:21 | 2026-02-11 20:14 | 53 | 103 | RJ45 cable cleaned and fixed properly | Completed | Maintainer | N/a | N/a | Network Back Online
19 | NA | NA | 2026-02-12 | SAL-ENC26-CE-01 | Vishnu/Amr | Communication betweeen NMS and NE is Abnormal | Device Down | NA |  | zone 56 | 51.2478413 25.1435454 | Outside Doha | P2 - High | 2026-02-12 17:16 | 2026-02-12 17:18 | 2 | 2026-02-12 17:18 | 2026-02-12 17:39 | 21 | 23 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
20 | NA | NA | 2026-02-14 | SAL-ENC20-CE-01,SAL-ENC14-CE-01,SAL-ENC20-UPE-02 | Vishnu/Amr | Communication betweeen NMS and NE is Abnormal | Device Down | NA |  | zone 56 | 51.3063942 25.164986 | Outside Doha | P2 - High | 2026-02-14 16:22 | 2026-02-14 16:25 | 3 | 2026-02-14 16:25 | 2026-02-14 16:54 | 29 | 32 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
21 | Sirti-WAN-R3-Ticket-01 | NA | 2026-02-15 | P028C2-ENC18-CE-01,P028C2-ENC25-CE-01,P028C2-ENC25-UPE-01 | Vishnu/Amr | Communication betweeen NMS and NE is Abnormal | Device Down | FLM visited the site and found no kahramaa power in cabinet as well as FP |  | Zone 18 | 25.28983, 51.51513 | Inside Doha | P2 - High | 2026-02-15 07:13 | 2026-02-15 07:15 | 2 | 2026-02-15 07:20 | 2026-02-15 08:48 | 88 | 95 | FLM Team contacted kharamaa and they restored the power | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
22 | Sirti-WAN-R3-Ticket-02 | NA | 2026-02-15 | SAL-ENC45-CE-01 | Vishnu/Amr | Communication betweeen NMS and NE is Abnormal | Device Down | FLM visited the site and found no kahramaa power in cabinet as well as FP |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P2 - High | 2026-02-15 07:44 | 2026-02-15 07:46 | 2 | 2026-02-15 08:31 | 2026-02-15 12:06 | 215 | 262 | Power restored by kharamaa team raised a ticket.Ref No-261100006258 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
23 | Sirti-WAN-R3-Ticket-03 | NA | 2026-02-15 | 22FEB-ENC25-CE-01 | Saleem/Amr | Link Down | Link Down | FLM visited the site and found port 05 down which is connected to LAN access switch |  | Zone 51 | 25.31832397, 51.47088144 | Outside Doha | P3 - Medium | 2026-02-15 11:38 | 2026-02-15 11:47 | 9 | 2026-02-15 11:47 | 2026-02-15 13:08 | 81 | 90 | The Alarm was cleared after LAN device came up | Completed | Maintainer | N/a | N/a | Network Back Online
24 | Sirti-WAN-R3-Ticket-04 | NA | 2026-02-16 | P010-ENC61-CE-01,P010-ENC64-CE-01 | Amr | Communication betweeen NMS and NE is Abnormal | Device Down | NA |  | Zone 57 | 51.4699752, 25.170097 | Outside Doha | P2 - High | 2026-02-16 09:23 | 2026-02-16 09:24 | 1 | 2026-02-16 09:24 | 2026-02-16 09:40 | 16 | 17 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
25 | Sirti-WAN-R3-Ticket-05 | NA | 2026-02-17 | P012-ENC97-UPE-02 | Vishnu/Haroon | Communication betweeen NMS and NE is Abnormal | Device Down | MCB was tripped at SMDB |  | Zone 56 | 25.1926322 51.4542203 | Outside Doha | P2 - High | 2026-02-17 16:37 | 2026-02-17 16:41 | 4 | 2026-02-17 17:02 | 2026-02-17 22:36 | 334 | 359 | FLM Turned on the CB and device restored | Completed | Non-maintainer | Access | Got the key from the Tunnel contractor and turned on the CB | Network Back Online
26 | Sirti-WAN-R3-Ticket-06 | NA | 2026-02-20 | P023C2-ENC16-CE-01 & P023C2-ENC16-UPE-02 | Aneesh/Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | P023C2-ENC16-CE-01 & P023C2-ENC16-UPE-02 unreachable from eSite |  | Zone 82 | 25.228079 51.307359 | Outside Doha | P2 - High | 2026-02-20 04:33 | 2026-02-20 04:42 | 9 | 2026-02-20 06:50 | 2026-02-20 07:10 | 20 | 157 | FLM Turned on the CB and devices restored | Completed | Maintainer | N/a | N/a | Network Back Online
27 | Sirti-WAN-R3-Ticket-07 | NA | 2026-02-20 | SAL-ENC20-CE-01 | Mastan/Adil | Node Down | Device Down | Port Down at CE Connected to Lan 2 Switch |  | Zone 82 | 25.164986, 51.3063942 | Outside Doha | P2 - High | 2026-02-20 08:48 | 2026-02-20 09:00 | 12 | 2026-02-20 09:00 | 2026-02-20 09:04 | 4 | 16 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
28 | Sirti-WAN-R3-Ticket-08 | NA | 2026-02-21 | RMC-P003 &SOC-P003 &P004-SOC PRI | Haroon/Masthan | Ethernet link down | Link Down | Eth link down RMC-P003 &SOC-P003 &P004-SOC PRI due QNBN activity on the link | - | Zone 66 | 25.3730597 51.5247872 | Outside Doha | P3 - Medium | 2026-02-21 12:21 | 2026-02-21 12:24 | 3 | 2026-02-21 12:24 | 2026-02-21 16:26 | 242 | 245 | Activity was finished and link was restored | Completed | Non-maintainer | 3rd Party | QNBN activity on the link | Network Back Online
29 | Sirti-WAN-R3-Ticket-09 | NA | 2026-02-22 | P028C2-ENC04-CE-01-OMC LOCAL | AMR / Vishnu | Communication betweeen NMS and NE is Abnormal | Device Down | NA | - | Zone 13 | 25.2791625° 51.5290008° | Inside Doha | P2 - High | 2026-02-22 10:32 | 2026-02-22 10:35 | 2.8333 | 2026-02-22 10:35 | 2026-02-22 10:44 | 9 | 11.8333 | Alarm Auto Cleared before flm visit the site | Completed | Maintainer | N/a | N/a | Network Back Online
30 | Sirti-WAN-R3-Ticket-10 | NA | 2026-02-22 | RMC-ENC-NMS-SW-01 SERVER | AMR / Erick | Link Down | Link Down | TTG team was working at RMC Datacenter on RMC-ENC-NMS-SW-01 SERVER as a part of snag clearanace | - | Zone 58 | 25.2410344° 51.4752267° | Outside Doha | P3 - Medium | 2026-02-22 11:52 | 2026-02-22 11:53 | 1 | 2026-02-22 11:52 | 2026-02-22 12:03 | 11.25 | 11.25 | Alarm Auto Cleared | Completed | Non-maintainer | 3rd Party | TTG team was working at RMC Datacenter | Network Back Online
31 | Sirti-WAN-R3-Ticket-11 | NA | 2026-02-22 | RAA_SEC | AMR / Haroon / Erick | Port Module Offline | One Power Source is Down | Power cable loose between DWDM and PDU | - | Zone 18 | 25.285228, 51.551657 | Inside Doha | P3 - Medium | 2026-02-22 10:54 | 2026-02-22 10:54 | 0 | 2026-02-22 10:54 | 2026-02-22 15:24 | 269 | 269 | FLM Visit the site and found the low voltage and fix the power source | Completed | Maintainer | N/a | N/a | Network Back Online
32 | Sirti-WAN-R3-Ticket-12 | NA | 2026-02-23 | P060-ENC18-UPE-01 | HAROON | High Temprature | LPU Board 2 | Boards Temprature higher than the upper threshold | - | Zone 69 | 25.4042479° 51.4923233° | Outside Doha | P3 - Medium | 2026-02-23 14:28 | 2026-02-23 14:30 | 2 | 2026-02-23 14:30 | 2026-02-23 14:38 | 8 | 10 | Alarm Auto Cleared before flm visit the site | Completed | Maintainer | N/a | N/a | Network Back Online
33 | Sirti-WAN-R3-Ticket-13 | NA | 2026-02-24 | P023C3-ENC174-UPE02 & P023C3-ENC174-CE 01 | Adel / Umair | Communication betweeen NMS and NE is Abnormal | Device Down | Breaker off from the FP side | - | Zone 94 | 25.01688 , 51.49047 | Outside Doha | P2 - High | 2026-02-24 03:48 | 2026-02-24 03:52 | 5 | 2026-02-24 05:01 | 2026-02-24 05:20 | 19.5 | 92.5 | MCB was tripped , FLM switched on the MCB | Completed | Maintainer | N/a | N/a | Network Back Online
34 | Sirti-WAN-R3-Ticket-14 | NA | 2026-02-24 | DUK-ENC04-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | NA | - | Zone 58 | 25.3809325° 51.2215135° | Outside Doha | P2 - High | 2026-02-24 10:23 | 2026-02-24 10:29 | 6 | 2026-02-24 10:29 | 2026-02-24 10:46 | 16.2833 | 22.2833 | Alarm Auto Cleared | Completed | Maintainer | N/a | N/a | Network Back Online
35 | Sirti-WAN-R3-Ticket-15 | NA | 2026-02-24 | DUK-ENC06-CE-01 | AMR | Link Down | Link Down | NA | - | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | P3 - Medium | 2026-02-24 11:47 | 2026-02-24 11:47 | 0 | 2026-02-24 11:47 | 2026-02-24 12:12 | 24.7333 | 24.7333 | Alarm Auto Cleared | Completed | Maintainer | N/a | N/a | Network Back Online
36 | Sirti-WAN-R3-Ticket-16 | NA | 2026-02-24 | P060-ENC18-UPE-01 | HAROON\Masthan | High Temprature | LPU Board 2 Heatup | Boards Temprature higher than the upper threshold | - | Zone 70 | 25.388045, 51.488990 | Outside Doha | P3 - Medium | 2026-02-24 13:09 | 2026-02-24 13:10 | 1 | 2026-02-24 13:30 | 2026-02-24 15:21 | 111 | 132 | FLM Visit the site and Turn on the AC Breaker and restore the Cooling | Completed | Maintainer | N/a | N/a | Network Back Online
37 | Sirti-WAN-R3-Ticket-17 | NA | 2026-02-25 | P059-C1-ENC23-CE-01 P059-C1-ENC23-UPE-02 P059-C1-ENC04-UPE-01 P059-C1-ENC42-CE-01 | AMR / Vishnu | Communication betweeen NMS and NE is Abnormal | Device Down / Link Down | There was no power supply in main terminals of DGME-23 | - | Zone 71 | 25.451633, 51.409080 | Outside Doha | P2 - High | 2026-02-25 08:13 | 2026-02-25 08:14 | 1 | 2026-02-25 08:57 | 2026-02-25 10:20 | 83.25 | 127.25 | Switched the Circuit from Primary to Secondary in ATS at Feeder side(ITS FP-16) | Completed | Maintainer | N/a | N/a | Network Back Online
38 | Sirti-WAN-R3-Ticket-18 | NA | 2026-02-26 | DUK-ENC12-CE-01 | AMR / Vishnu | Link Down | Link Down | Other Ashghal Contractor (ITS Qatar) was doing the maintenance for PTZ Camera)-On NMS port down GE1/0/15 -Huawei Switch | - | Zone 80 | 25.430216, 51.149749 | Outside Doha | P3 - Medium | 2026-02-26 08:04 | 2026-02-26 08:06 | 2 | 2026-02-26 08:04 | 2026-02-26 08:42 | 37.7667 | 37.7667 | FME arrived at the site and found that ITS Qatar was performing maintenance on the PTZ camera. After the maintenance was completed, the alarm was cleared-Verified the ports in Huawei Switch, all were working well | Completed | Non-maintainer | 3rd Party | ITS Qatar was performing maintenance | Network Back Online
39 | Sirti-WAN-R3-Ticket-19 | NA | 2026-02-26 | SAL-ENC45-CE-01 | AMR / Vishnu | Link Down | Link Down | NA -On NMS port down GE1/0/15 -Huawei Switch | - | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-02-26 08:24 | 2026-02-26 08:26 | 2 | 2026-02-26 08:26 | 2026-02-26 08:47 | 21 | 23 | FME arrived Verified the ports in Huawei Switch, all were working well- Link went down and restored after 22 min 49 sec | Completed | Maintainer | N/a | N/a | Network Back Online
40 | Sirti-WAN-R3-Ticket-20 | NA | 2026-02-26 | DUK-ENC16-CE-01 | AMR / Vishnu | Link Down | Link Down | NA -On NMS port down GE1/0/9 -Huawei Switch | - | Zone 80 | 25.432295, 51.110656 | Outside Doha | P3 - Medium | 2026-02-26 09:02 | 2026-02-26 09:04 | 2 | 2026-02-26 09:11 | 2026-02-26 09:25 | 14 | 23 | FME arrived Verified the ports in Huawei Switch, all were working well- Link went down and restored | Completed | Maintainer | N/a | N/a | Network Back Online
41 | Sirti-WAN-R3-Ticket-21 | NA | 2026-02-26 | SAL-ENC50-CE-01 | AMR / Vishnu | Link Down | Link Down | NA -On NMS port down GE1/0/10 -Huawei Switch | - | Zone 96 | 24.951308, 50.999354 | Outside Doha | P3 - Medium | 2026-02-26 10:21 | 2026-02-26 10:21 | 0 | 2026-02-26 10:29 | 2026-02-26 10:45 | 16 | 24 | FME arrived Verified the ports in Huawei Switch, all were working well- Link went down and restored | Completed | Maintainer | N/a | N/a | Network Back Online
42 | Sirti-WAN-R3-Ticket-22 | NA | 2026-02-26 | P008-C3-ENC19-CE-01 P008-C3-ENC09-CE-01 P008-C3-ENC05-CE-01 P008-C3-ENC07-CE-01 P008-C3-ENC04-CE-01 P008-C3-ENC01-CE-01 | AMR / Vishnu | Communication betweeen NMS and NE is Abnormal | Communication betweeen NMS and NE is Abnormal | Issue Esclated to Imran (SALAM TECH) by call and whats app messages | - | - | - | - | P2 - High | 2026-02-26 10:31 | 2026-02-26 10:31 | 0 | 2026-02-26 10:31 | 2026-02-26 11:35 | 64.1833 | 64.1833 | Issue Esclated to Imran (SALAM TECH) by call and whats app messages - All alarms got cleared | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
43 | Sirti-WAN-R3-Ticket-23 | NA | 2026-02-27 | P010-ENC01-CE-01 | HAROON / Patric | Heat Alarm | SFP Interface Heat Alarm | Optical Module temp too high | - | Zone 81 | 25.139881, 51.407393 | Outside Doha | P3 - Medium | 2026-02-27 12:08 | 2026-02-27 12:11 | 3 | 2026-02-27 12:11 | 2026-02-27 15:35 | 204 | 207 | Alarm is about SFP interface heatup overall device stats are normal, no Service Effected.alarms got cleared | Completed | Maintainer | N/a | N/a | Network Back Online
44 | Sirti-WAN-R3-Ticket-24 | NA | 2026-02-28 | SAL-ENC67-CE-01 | AMR | Link Down | Link Down | NA | - | Zone 96 | 24.7761642° 50.8665552° | Outside Doha | P3 - Medium | 2026-02-28 11:06 | 2026-02-28 11:06 | 0 | 2026-02-28 11:06 | 2026-02-28 11:23 | 17.05 | 17.05 | Link went down and restored Auto | Completed | Maintainer | N/a | N/a | Network Back Online
45 | Sirti-WAN-R3-Ticket-25 | NA | 2026-03-03 | DUK-ENC34-CE-01 | AMR | Link Down | Link Down | NA | - | Zone 72 | 25.4537767 50.8835078 | Outside Doha | P3 - Medium | 2026-03-03 12:18 | 2026-03-03 12:18 | 0 | 2026-03-03 12:18 | 2026-03-03 12:45 | 27.05 | 27.05 | Issue esclated to RMC team and they have update Team is doing PM for End device | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
46 | Sirti-WAN-R3-Ticket-26 | NA | 2026-03-04 | RAA-TCR-USG-02 / DWDM RAA_SEC | AMR | PWR Module Stopped Working | Power Module Power off | PDU Was OFF | - | Zone 18 | 25.28522778 51.55165688 | Inside Doha | P3 - Medium | 2026-03-04 08:22 | 2026-03-04 08:24 | 2 | 2026-03-04 09:00 | 2026-03-04 09:36 | 36.7667 | 74.7667 | FLM Turned on the CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online
47 | Sirti-WAN-R3-Ticket-27 | NA | 2026-03-04 | DWDM RAA_SEC | AMR | ASH_WDM_RAA-P015-OSC_Protection ASH_WDM_RAA-P012-OSC_Protection ASH_WDM_SOC-P012-OCH-CH-54_Protection_L ASH_WDM_RMC-P012-OCH-CH-56_Protection_L ASH_WDM_SOC-P015-OCH-CH-58_Protection_S ASH_WDM_RMC-P015-OCH-CH-60_Protection_L | RAA_Sec Subrack 2 was down due to power issue | PWR cable at PDU side was loose | - | Zone 18 | 25.28522778 , 51.55165688 | Inside Doha | P3 - Medium | 2026-03-04 09:20 | 2026-03-04 09:20 | 0 | 2026-03-04 09:41 | 2026-03-04 09:52 | 11.7833 | 32.7833 | FLM fixed the loose power cable connection by cable tie /to be plan for PDU replacement | Completed | Maintainer | N/a | N/a | Network Back Online
48 | Sirti-WAN-R3-Ticket-28 | NA | 2026-03-08 | - P004-TMC-NPE-01 - P004_Pri - P004_Sec | Abubaker | Power Module Powered off | Power Module Power off | khahromaa power shutdown | - | Zone 51 | 25.319385, 51.352255 | Outside Doha | P3 - Medium | 2026-03-08 05:23 | 2026-03-08 05:28 | 5.4833 | 2026-03-08 06:01 | 2026-03-08 07:01 | 60.8333 | 98.8333 | Main Power was down due to power outage from Kharahma side, Alarms cleared after Kharahma power recovered by Kharahma team | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
49 | Sirti-WAN-R3-Ticket-29 | NA | 2026-03-08 | P004-ENC43-UPE-02 P004-ENC43-CE-01 P023C2-ENC43-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no PWR at ENC / FP CB was tripped | - | Zone 51 | 25.319385, 51.352255 | Outside Doha | P2 - High | 2026-03-08 17:23 | 2026-03-08 17:27 | 4 | 2026-03-08 18:02 | 2026-03-08 18:19 | 16.5 | 55.5 | The FME team reached the site and found that there was no power in the ENC cabinet. Upon checking the FP cabinet, they found that the main circuit breaker (CB) was in the OFF (tripped) state. The CB was switched ON, after which all devices were restored and the alarms were cleared | Completed | Maintainer | N/a | N/a | Network Back Online
50 | Sirti-WAN-R3-Ticket-30 | NA | 2026-03-09 | P010-ENC61-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | - | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-03-09 08:00 | 2026-03-09 08:06 | 6.25 | 2026-03-09 09:02 | 2026-03-09 09:45 | 43.5167 | 105.5167 | there was no UPS output power , FLM Turned on the UPS | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
51 | Sirti-WAN-R3-Ticket-31 | NA | 2026-03-09 | P004-TMC-NPE-01 P004-sec P004-pri | Adel | power module stopped working , power fail | power fail | alarm is auto clear before visiting the site | - | Zone 51 | 25.319385, 51.352255 | Outside Doha | P3 - Medium | 2026-03-09 10:14 | 2026-03-09 10:17 | 3.1833 | 2026-03-09 10:17 | 2026-03-09 10:29 | 12.3333 | 15.5167 | alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
52 | Sirti-WAN-R3-Ticket-32 | NA | 2026-03-09 | P010-ENC61-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | - | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-03-09 10:36 | 2026-03-09 10:40 | 4.2667 | 2026-03-09 11:03 | 2026-03-09 11:14 | 10.9667 | 37.9667 | there was no UPS output power , FLM Turned on the UPS | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
53 | Sirti-WAN-R3-Ticket-33 | NA | 2026-03-09 | P010-ENC61-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | - | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-03-09 12:14 | 2026-03-09 12:18 | 4 | 2026-03-09 13:04 | 2026-03-09 13:26 | 21.9 | 71.9 | there was no UPS output power , FLM Turned on the UPS, disconnected the AC from the UPS | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
54 | Sirti-WAN-R3-Ticket-34 | NA | 2026-03-09 | P010-ENC61-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | NA | - | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-03-09 15:38 | 2026-03-09 15:38 | 0 | 2026-03-09 15:38 | 2026-03-09 15:49 | 10.9167 | 10.9167 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
55 | Sirti-WAN-R3-Ticket-35 | NA | 2026-03-10 | P029C2-ENC05-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | tripped CB | - | Zone 39 | 25.281278° ,51.503972° | Inside Doha | P2 - High | 2026-03-10 07:33 | 2026-03-10 07:36 | 2.9 | 2026-03-10 08:20 | 2026-03-10 09:13 | 52.7667 | 99.7667 | FLM switched on tripped CB | Completed | Maintainer | N/a | N/a | Network Back Online
56 | Sirti-WAN-R3-Ticket-36 | NA | 2026-03-10 | SAL-ENC63-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | alarm is auto clear before visiting the site | - |  | 24.8301249° ,50.8705931° | Outside Doha | P2 - High | 2026-03-10 12:15 | 2026-03-10 12:18 | 3.3167 | 2026-03-10 12:18 | 2026-03-10 13:12 | 54.3667 | 57.6833 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
57 | Sirti-WAN-R3-Ticket-37 | NA | 2026-03-11 | P023C2-Enc11-CE-01 | Aaqib | VRRP switchover performed | VRRP switchover performed | Alarm auto cleared. Suspecting link fluctuation | - | Zone 96 | 25.325262° , 51.329176° | Outside Doha | P4 - Low | 2026-03-11 04:03 | 2026-03-11 04:05 | 2 | 2026-03-11 04:05 | 2026-03-11 04:07 | 2 | 4 | Alarm auto cleared | Completed | Maintainer | N/a | N/a | Network Back Online
58 | Sirti-WAN-R3-Ticket-38 | NA | 2026-03-11 | P010-ENC61-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | - | Zone 53 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-03-11 07:28 | 2026-03-11 07:34 | 6 | 2026-03-11 08:38 | 2026-03-11 09:50 | 71.95 | 141.95 | FLM disconnected the AC from UPS and connected it directly to CB | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
59 | Sirti-WAN-R3-Ticket-39 | NA | 2026-03-11 | P010-ENC61-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | No power in cabinet | - | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-03-11 15:02 | 2026-03-11 15:05 | 3 | 2026-03-11 15:43 | 2026-03-11 16:14 | 30.6 | 71.6 | FLM disconnected the AC from UPS and connected it directly to CB , team is monitoring the UPS behavior after the action | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
60 | Sirti-WAN-R3-Ticket-40 | NA | 2026-03-12 | P010-ENC61-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | DEVICE DOWN DUE TO UPS FAULTY | - | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-03-12 09:19 | 2026-03-12 09:21 | 2 | 2026-03-12 09:57 | 2026-03-12 10:50 | 53.2667 | 91.2667 | UPS FAULTY need to replace .for now remove the UPS connetion temporary now we directly connect the device | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
61 | Sirti-WAN-R3-Ticket-41 | NA | 2026-03-12 | SAL-ENC56-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | NA | - | Zone 96 | 24.891173, 50.938318 | Outside Doha | P2 - High | 2026-03-12 10:52 | 2026-03-12 10:53 | 1 | 2026-03-12 10:53 | 2026-03-12 11:38 | 45.1167 | 46.1167 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
62 | Sirti-WAN-R3-Ticket-42 | NA | 2026-03-13 | P008C2-ENC01-CE-01 | AMR | Link Down | Link Down | Cable Loose | - | Zone 56 | 25.236901, 51.521726 | Outside Doha | P3 - Medium | 2026-03-13 10:52 | 2026-03-13 10:57 | 5 | 2026-03-13 11:00 | 2026-03-13 11:11 | 11.6167 | 19.6167 | FME clean the cable and fix it properly | Completed | Maintainer | N/a | N/a | Network Back Online
63 | Sirti-WAN-R3-Ticket-43 | NA | 2026-03-15 | P011-Enc26-UPE-01 P011-Enc26-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | As per Logs, there was power interruption at site | - | Zone 50 | 25.22234, 51.542 | Outside Doha | P2 - High | 2026-03-15 03:25 | 2026-03-15 03:26 | 1 | 2026-03-15 03:26 | 2026-03-15 03:31 | 5 | 6 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Devices Back Online
64 | Sirti-WAN-R3-Ticket-44 | NA | 2026-03-17 | SAL-ENC14-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet | - | Zone 96 | 25.1858801° 51.3628538° | Outside Doha | P2 - High | 2026-03-17 09:59 | 2026-03-17 10:01 | 2 | 2026-03-17 10:01 | 2026-03-17 10:49 | 47.2833 | 49.2833 | The Kahramaa team was working at FP. Once they completed their work and cable termination, power was restored, all devices came up, and all alarms were cleared. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
65 | Sirti-WAN-R3-Ticket-45 | NA | 2026-03-18 | P006-ENC02-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | As per Logs, there was power interruption at site | - | Zone 56 | 25.2190399° 51.4369501° | Outside Doha | P2 - High | 2026-03-18 09:59 | 2026-03-18 10:05 | 5.3167 | 2026-03-18 10:05 | 2026-03-18 10:10 | 5 | 10.3167 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
66 | Sirti-WAN-R3-Ticket-46 | NA | 2026-03-19 | P010-ENC01-CE-01 | Abubaker | Optical Model temperature too high | SFP Alarm | Alarm cleared automatically by itself after 1h & 11mins | - | Zone 81 | 25.139881, 51.407393 | Outside Doha | P3 - Medium | 2026-03-19 14:58 | 2026-03-19 14:59 | 1.4833 | 2026-03-19 15:21 | 2026-03-19 16:09 | 48.3 | 71.7833 | Alarm auto cleared | Completed | Maintainer | N/a | N/a | Devices Back Online
67 | Sirti-WAN-R3-Ticket-47 | NA | 2026-03-20 | P003-ENC10-CE-DGME-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet due to the failure of SLFP cabient which is uder RF001 | - | Zone 66 | 25.3735283 51.5285481 | Outside Doha | P2 - High | 2026-03-20 09:08 | 2026-03-20 09:12 | 3.1167 | 2026-03-20 09:31 | 2026-03-20 13:49 | 257.95 | 280.0667 | Sirti MENAA has communicated RMC to request RF001 to fix SLFP Panel, after they rectify the panel, the power back to ITS-FP and all nodes back online | Completed | Non-maintainer | 3rd Party | RF001 | Network Back Online
68 | Sirti-WAN-R3-Ticket-48 | NA | 2026-03-21 | P003-Enc10-CE-DGME-01 | Aaqib/Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet due to the failure of SLFP cabient which is uder RF001 | - | Zone 66 | 25.3735283 51.5285481 | Outside Doha | P2 - High | 2026-03-21 07:42 | 2026-03-21 07:46 | 3.8 | 2026-03-21 08:25 | 2026-03-21 18:01 | 575.3667 | 618.8167 | Sirti MENAA has communicated RMC to request RF001 to fix SLFP Panel, after they rectify the panel, the power back to ITS-FP and all nodes back online | Completed | Non-maintainer | 3rd Party | RF001 | Network Back Online
69 | Sirti-WAN-R3-Ticket-49 | NA | 2026-03-21 | Sal-Enc45-CE-01 | Aaqib | Link Down | Link down | Link down towards LAN |  | Zone 83 | 25.005944° 51.042739 | Outside Doha | P3 - Medium | 2026-03-21 12:59 | 2026-03-21 12:59 | 0 | 2026-03-21 12:59 | 2026-03-21 13:05 | 6.05 | 6.05 | Link auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
70 | Sirti-WAN-R3-Ticket-50 | NA | 2026-03-21 | SAL-ENC14-CE-01 | Sanket | Link Down | LAN Link down | Link down towards LAN |  | Zone 83 | 25.005944° 51.042739° | Outside Doha | P3 - Medium | 2026-03-21 19:26 | 2026-03-21 19:26 | 0 | 2026-03-21 19:26 | 2026-03-21 19:30 | 3.9167 | 3.9167 | Link auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
71 | Sirti-WAN-R3-Ticket-51 | NA | 2026-03-21 | P003-ENC10-CE-DGME-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet. |  | Zone 66 | 25.3735283 51.5285481 | Outside Doha | P2 - High | 2026-03-21 20:41 | 2026-03-21 20:43 | 2 | 2026-03-21 20:52 | 2026-03-21 20:57 | 4.35 | 15.3 | Temperory generator removed and supply given from Kharamaa. | Completed | Non-maintainer | N/a | State Kahramaa | Network Back Online
72 | Sirti-WAN-R3-Ticket-52 | NA | 2026-03-21 | SAL-ENC20-CE-01 | Sanket | Link Down | LAN Link down | Link down towards LAN |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-03-21 20:52 | 2026-03-21 20:52 | 0 | 2026-03-21 20:53 | 2026-03-21 21:00 | 7.0833 | 8.0833 | Link auto restored. The link is down towards LAN | Completed | Maintainer | N/a | N/a | Network Back Online
73 | Sirti-WAN-R3-Ticket-53 | NA | 2026-03-21 | P003-ENC37-CE-DGME-01 | Sanket/Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | There was no power on the outgoing-1 of the PSU | - | Zone 65 | 25.3364931° 51.51767° | Outside Doha | P2 - High | 2026-03-21 21:33 | 2026-03-21 21:36 | 3.4167 | 2026-03-21 23:00 | 2026-03-21 23:32 | 31.8 | 119.3333 | We checked outgoing-2, and it's found sufficient, we connect the switch to outgoing-2 of PSU | Completed | Maintainer | N/a | N/a | Network Back Online
74 | Sirti-WAN-R3-Ticket-54 | NA | 2026-03-23 | IE5000-1003 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Device Restored before team visit | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-03-23 01:24 | 2026-03-23 01:31 | 7.25 | 2026-03-23 01:24 | 2026-03-23 05:39 | 255.1333 | 255.1333 | that switch is LAN switch managed by WAN NMS , team doesnot have the location of the switch and that escalated to 3rd party , at time 5:38 am the devices come back online without visiting | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hichem
75 | Sirti-WAN-R3-Ticket-55 | NA | 2026-03-23 | P017C2-ENC23-CE01 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found MCB was tripped | - | Zone 57 | 25.1702778° 51.4710278° | Outside Doha | P2 - High | 2026-03-23 02:11 | 2026-03-23 02:17 | 6.3 | 2026-03-23 04:23 | 2026-03-23 04:28 | 4.6167 | 137.0833 | FLM switched on cabinet main CB , tripped due to rain | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
76 | Sirti-WAN-R3-Ticket-56 | NA | 2026-03-23 | DUK-ENC30-CE01 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no kharama power on site. | - | Zone 85 | 25.4637854° 50.930279° | Outside Doha | P2 - High | 2026-03-23 02:11 | 2026-03-23 02:14 | 2.8167 | 2026-03-23 02:39 | 2026-03-23 08:53 | 374.0333 | 402.0333 | FLM visit the site and found that no kharama power on site. Ticket (Ref # 261100010894) is raised with kahrama. Device restored after kahahrama power restoration | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
77 | Sirti-WAN-R3-Ticket-57 | NA | 2026-03-23 | P008C2-ENC01-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | cabinet main CB is off | - | Zone 56 | 25.2369009° 51.521726° | Outside Doha | P2 - High | 2026-03-23 02:23 | 2026-03-23 02:26 | 3.4 | 2026-03-23 02:36 | 2026-03-23 04:23 | 107.8 | 120.8 | FLM switched on cabinet main CB , tripped due to rain | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
78 | Sirti-WAN-R3-Ticket-58 | NA | 2026-03-23 | P007C2-ENC82-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Main UPS CB is tripped | - | Zone 52 | 25.3045066° 51.4548113° | Outside Doha | P2 - High | 2026-03-23 02:39 | 2026-03-23 02:49 | 9.8667 | 2026-03-23 05:49 | 2026-03-23 05:55 | 6.5167 | 196.0833 | FLM switched on main UPS CB | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
79 | Sirti-WAN-R3-Ticket-59 | NA | 2026-03-23 | P015-ENC19A-CE-01 | Adel | Power Module stopped working | Power Module stopped working | Team found the CB powering up Source B is faulty | - | Zone 91 | 25.1328013° 51.5759416° | Outside Doha | P3 - Medium | 2026-03-23 02:47 | 2026-03-23 02:52 | 4.6333 | 2026-03-23 03:12 | 2026-03-23 07:50 | 277.6833 | 302.6833 | The main CB has been replaced | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
80 | Sirti-WAN-R3-Ticket-60 | NA | 2026-03-23 | P007C2-ENC99-UPE02 P007C2-ENC99-CE01 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found that CB was tripped | - | Zone 52 | 25.2967109° 51.4488814° | Outside Doha | P2 - High | 2026-03-23 06:17 | 2026-03-23 06:20 | 2.7667 | 2026-03-23 07:03 | 2026-03-23 07:18 | 15.4333 | 60.9333 | FLM visit the site and was found that CB was tripped. Devices restored after turning ON CB | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
81 | Sirti-WAN-R3-Ticket-61 | NA | 2026-03-23 | CRR-ENC02-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 18 | 25.2834083°, 51.5496912° | Inside Doha | P2 - High | 2026-03-23 09:09 | 2026-03-23 09:12 | 2.7333 | 2026-03-23 09:12 | 2026-03-23 09:14 | 2.35 | 5.0833 | As per log, there was khahrama interruption at site. | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
82 | Sirti-WAN-R3-Ticket-62 | NA | 2026-03-23 | P042-ENC08-CE-01 | Sanket | Link Down | LAN Link down | port error disable GE 1/13 | - | Zone 49 | 25.226270° 51.590859° | Outside Doha | P3 - Medium | 2026-03-23 17:11 | 2026-03-23 17:13 | 2.3167 | 2026-03-23 17:13 | 2026-03-23 17:19 | 5.5833 | 7.9 | The port is in error disable. After shut and unshut the port link became normal. The link is down towards LAN | Completed | Maintainer | N/a | N/a | Network Back Online
83 | Sirti-WAN-R3-Ticket-63 | NA | 2026-03-23 | DUK-ENC30-CE-01 | Sanket | Link Down | LAN Link down | The link is down towards the LAN ( D-NODE-28 is down) | - | Zone 85 | 25°27'16.48 50°57'15.07 | Outside Doha | P3 - Medium | 2026-03-23 17:46 | 2026-03-23 17:51 | 5 | 2026-03-23 18:33 | 2026-03-23 20:51 | 138.4333 | 185.2333 | As per LAN team, D-Node 28 is down and No Kharamaa power available in the cabinet. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
84 | Sirti-WAN-R3-Ticket-64 | NA | 2026-03-23 | SAL-ENC32-CE-01 | Sanket | Link Down | LAN Link down | Link down towards LAN | - | Zone 82 | 25.1165799° 51.1812367° | Outside Doha | P3 - Medium | 2026-03-23 19:39 | 2026-03-23 19:41 | 2.8167 | 2026-03-23 19:41 | 2026-03-23 19:45 | 3.35 | 6.1667 | Link auto restored. The link is down towards LAN | Completed | Maintainer | N/a | N/a | Network Back Online
85 | Sirti-WAN-R3-Ticket-65 | NA | 2026-03-23 | IE5000-2302 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 23 | 25.272861° 51.510861° | Inside Doha | P2 - High | 2026-03-23 22:19 | 2026-03-23 22:21 | 2 | 2026-03-23 22:21 | 2026-03-23 22:22 | 1.2 | 3.2 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
86 | Sirti-WAN-R3-Ticket-66 | NA | 2026-03-24 | SAL-ENC09-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | No power in 1 phase of Khahrama | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-24 01:11 | 2026-03-24 01:17 | 5.5833 | 2026-03-24 02:06 | 2026-03-24 03:20 | 74.65 | 129 | - The node was down due to unavailability of the power in 2 phases. - Kharahma Service Request raised. - As a WA, the node connected to the phase line having power. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
87 | Sirti-WAN-R3-Ticket-67 | NA | 2026-03-24 | SAL-ENC50-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Team found that CB was tripped | - | Zone 96 | 24.9513076° 50.9993542° | Outside Doha | P2 - High | 2026-03-24 09:46 | 2026-03-24 09:49 | 3.2167 | 2026-03-24 09:54 | 2026-03-24 10:48 | 53.4667 | 61.85 | FLM visit the site and found MCB at FP was tripped. Device restored after switching ON MCB at FP. | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
88 | Sirti-WAN-R3-Ticket-68 | NA | 2026-03-24 | P003-ENC10-CE-DGME-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Team found that CB was tripped | - | Zone 66 | 25.3735283 51.5285481 | Outside Doha | P2 - High | 2026-03-24 10:31 | 2026-03-24 10:33 | 2.0667 | 2026-03-24 11:45 | 2026-03-24 12:21 | 36.5833 | 109.9667 | FLM visit the site and found MCB at FP was tripped. Device restored after switching ON MCB at FP. | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
89 | Sirti-WAN-R3-Ticket-69 | NA | 2026-03-24 | P007C7P1-ENC01-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | Team found that CB was tripped | - | Zone 31 | 25.339487° 51.4610983° | Inside Doha | P2 - High | 2026-03-24 12:04 | 2026-03-24 12:06 | 2 | 2026-03-24 12:21 | 2026-03-24 15:51 | 210.3333 | 227.3333 | As per Slam Tech team, CB was tripped. Devices restored after turning ON CB | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
90 | Sirti-WAN-R3-Ticket-70 | NA | 2026-03-24 | DUK-ENC06-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | P2 - High | 2026-03-24 13:38 | 2026-03-24 13:46 | 8.1667 | 2026-03-24 13:46 | 2026-03-24 13:59 | 13.0333 | 21.2 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
91 | Sirti-WAN-R3-Ticket-71 | NA | 2026-03-25 | SAL-ENC50-CE-01 | Abubaker | Link Down | LAN Link down | The cable toward the CCTV is disconnected (GE 1/0/10) | - | Zone 96 | 24.9513076, 50.9993542 | Outside Doha | P3 - Medium | 2026-03-24 23:19 | 2026-03-24 23:27 | 7.8 | 2026-03-25 00:25 | 2026-03-25 01:20 | 55.05 | 120.85 | 3rd Party ccntractor ITSQ change the RJ45 connector at POE end and Port is up | Completed | Non-maintainer | 3rd Party | 3rd Party ccntractor | Port is up and alarm cleared | Khadar basha syed
92 | Sirti-WAN-R3-Ticket-72 | NA | 2026-03-25 | SAL-ENC50-CE-01 | Abubaker | Link Down | LAN Link down | RJ45 Connector was found faulty | - | Zone 96 | 24.9513076, 50.9993542 | Outside Doha | P3 - Medium | 2026-03-25 02:42 | 2026-03-25 02:48 | 5.8833 | 2026-03-25 02:48 | 2026-03-25 03:01 | 12.6667 | 18.55 | Auto clear before team visit | Completed | Maintainer | N/a | N/a | Port is up and alarm cleared
93 | Sirti-WAN-R3-Ticket-73 | NA | 2026-03-25 | DUK-ENC12-CE-01 | Abubaker | Link Down | LAN Link down | Short Circuit in 3 Phase khahrama connection | - | Zone 72 | 25.4322949° 51.1106559° | Outside Doha | P3 - Medium | 2026-03-25 03:53 | 2026-03-25 03:56 | 2.9667 | 2026-03-25 04:46 | 2026-03-25 06:24 | 97.3667 | 150.3167 | The cabinet power issue was caused by a short circuit between R/Y/B phases and Neutral in the power cable of Khahrama | Completed | Maintainer | N/a | N/a | Network Back Online | Umair Rahman
94 | Sirti-WAN-R3-Ticket-74 | NA | 2026-03-25 | SAL-ENC09-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB was found faulty | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-25 08:20 | 2026-03-25 08:24 | 4.4667 | 2026-03-25 09:01 | 2026-03-25 10:00 | 58.7833 | 100.6333 | Device was down due to faulty CB. Team change CB connection with spare CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online | Kwadwo Ofosu
95 | Sirti-WAN-R3-Ticket-75 | NA | 2026-03-25 | P029C2-ENC05-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | During PPM activity / AC compressor faulty when the team make AC CB ON - the main CB went OFF | - | Zone 39 | 25.281278 51.503972 | Inside Doha | P2 - High | 2026-03-25 12:50 | 2026-03-25 12:51 | 1 | 2026-03-25 12:54 | 2026-03-25 12:57 | 2.1 | 6.1 | During PPM activity / AC compressor faulty when the team make AC CB ON - the main CB went OFF /team make CB ON and all alarms got cleared | Completed | Maintainer | N/a | N/a | Network Back Online | Hecham
96 | Sirti-WAN-R3-Ticket-76 | NA | 2026-03-25 | P059C1-N2-ENC19-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 70 | 25.43425476° 51.412436° | Outside Doha | P2 - High | 2026-03-25 14:18 | 2026-03-25 14:22 | 4.45 | 2026-03-25 14:22 | 2026-03-25 14:24 | 2 | 6.45 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
97 | Sirti-WAN-R3-Ticket-77 | NA | 2026-03-26 | IE5000-1003 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Device Restored before team visit | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-03-26 06:36 | 2026-03-26 06:41 | 4.6333 | 2026-03-26 06:41 | 2026-03-26 06:58 | 16.5333 | 21.1667 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
98 | Sirti-WAN-R3-Ticket-78 | NA | 2026-03-26 | SAL-ENC20-CE-01 SAL-ENC20-UPE-02 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | QBC team is working at FP | - | Zone 82 | 25.164986° 51.3063942 | Outside Doha | P2 - High | 2026-03-26 11:06 | 2026-03-26 11:09 | 3.1 | 2026-03-26 11:09 | 2026-03-26 11:36 | 26.8833 | 29.9833 | QBC team is working at Fidder Piller | Completed | Non-maintainer | 3rd Party | 3rd Party ccntractor | Network Back Online | Patric
99 | Sirti-WAN-R3-Ticket-79 | NA | 2026-03-26 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Sub Main CB breaker tripping along with AC CB Due to AC Defect | - | Zone 20 | 25.30462 51.51743 | Inside Doha | P2 - High | 2026-03-26 10:15 | 2026-03-26 10:20 | 4.7333 | 2026-03-26 10:55 | 2026-03-26 11:08 | 13.05 | 52.7833 | Sub Main CB breaker Restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hichem
100 | Sirti-WAN-R3-Ticket-80 | NA | 2026-03-26 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Sub Main CB breaker tripping along with AC CB due to AC defect during PPM | - | Zone 20 | 25.30462 51.51743 | Inside Doha | P2 - High | 2026-03-26 12:34 | 2026-03-26 12:38 | 4 | 2026-03-26 12:38 | 2026-03-26 12:48 | 10.5 | 14.5 | Change AC Capacitor and deep cleaning of all AC components | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hichem
101 | Sirti-WAN-R3-Ticket-81 | NA | 2026-03-26 | SAL-ENC26-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | alarm is auto clear before visiting the site | - | Zone 81 | 25.1435454° 51.2478413° | Outside Doha | P2 - High | 2026-03-26 17:14 | 2026-03-26 17:16 | 1.7167 | 2026-03-26 17:14 | 2026-03-26 17:17 | 2.25 | 2.25 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online | -
102 | Sirti-WAN-R3-Ticket-82 | NA | 2026-03-26 | DUK-ENC24-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found no power inside cabinet | - | Zone 85 | 25.435778° 51.0066732° | Outside Doha | P2 - High | 2026-03-26 16:38 | 2026-03-26 16:40 | 1.9 | 2026-03-26 17:54 | 2026-03-26 18:19 | 24.8833 | 100.7833 | FLM switched on main CB that was tripped | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | sanjeewa
103 | Sirti-WAN-R3-Ticket-83 | NA | 2026-03-26 | DUK-ENC20-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | No Khahroma power at cabenit | - | Zone 72 | 25.427405° 51.0546006° | Outside Doha | P2 - High | 2026-03-26 17:46 | 2026-03-26 17:49 | 2.6333 | 2026-03-26 19:33 | 2026-03-26 23:19 | 226.3667 | 333 | Esclated to Kharahma & power was restored, all devices came up | Completed | Non-maintainer | Environmental & 3rd Party | Rain Event & State Kahramaa | Network Back Online | sanjeewa
104 | Sirti-WAN-R3-Ticket-84 | NA | 2026-03-26 | P060-ENC18-CE-GME-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | main Cabinet CB was tripped | - | Zone 69 | 25.4042479° 51.4923233° | Outside Doha | P2 - High | 2026-03-26 17:35 | 2026-03-26 17:40 | 4.5667 | 2026-03-26 20:02 | 2026-03-26 20:16 | 13.85 | 160.4167 | FLM switched on main CB that was tripped | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | najeeb
105 | Sirti-WAN-R3-Ticket-85 | NA | 2026-03-26 | SAL-ENC50-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power at cabinet | - | Zone 96 | 24.9513076° 50.9993542° | Outside Doha | P2 - High | 2026-03-26 18:17 | 2026-03-26 18:18 | 1.2167 | 2026-03-26 20:49 | 2026-03-26 21:15 | 26.4667 | 178.6833 | FLM switched on main CB at feeder pillar | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | hassan
106 | Sirti-WAN-R3-Ticket-86 | NA | 2026-03-26 | SAL-ENC45-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power inside cabinet | - | Zone 83 | 25.005944° 51.042739° | Outside Doha | P2 - High | 2026-03-26 18:20 | 2026-03-26 18:21 | 1.2833 | 2026-03-26 19:35 | 2026-03-26 20:04 | 28.7 | 103.9833 | FLM switched on main CB at feeder pillar | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | hassan
107 | Sirti-WAN-R3-Ticket-87 | NA | 2026-03-26 | SAL-ENC67-CE-01 | Adel | Link Down | LAN device down | No Kharahma Power at the LAN device | - | Zone 96 | 24.7761642° 50.8665552° | Outside Doha | P3 - Medium | 2026-03-26 18:28 | 2026-03-26 18:37 | 9.0167 | 2026-03-26 19:39 | 2026-03-26 23:44 | 245.0833 | 316.1 | Esclated to Kharahma & power was restored, all devices came up | Completed | Non-maintainer | Environmental & 3rd Party | Rain Event & State Kahramaa | Network Back Online | hassan
108 | Sirti-WAN-R3-Ticket-88 | NA | 2026-03-26 | P029C1-ENC02-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power inside cabinet | - | Zone 54 | 25.2779777° 51.4661648 | Outside Doha | P2 - High | 2026-03-26 18:48 | 2026-03-26 18:53 | 4.55 | 2026-03-26 21:31 | 2026-03-26 22:07 | 35.7 | 198.25 | FLM switched on main CB at feeder pillar & bypass the UPS as it is tripping the FB CB | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | aneesh
109 | Sirti-WAN-R3-Ticket-89 | NA | 2026-03-26 | SAL-ENC32-CE-01 | Adel | Farwarding Engine fail | Device hardware fault | No abonormalities found at site | - | Zone 82 | 25.1165799° 51.1812367° | Outside Doha | P3 - Medium | 2026-03-26 22:15 | 2026-03-26 22:25 | 9.55 | 2026-03-26 22:18 | 2026-03-27 00:15 | 116.6667 | 119.2167 | Performed a hardware reboot for the device | Completed | Non-maintainer | Environmental | Rain Event | Alarm Cleared | aneesh
110 | Sirti-WAN-R3-Ticket-90 | NA | 2026-03-28 | P028C2-Enc06-DGME-CE-01 | Aaqib | Link Down | 1x10G Link Down | Port TE 1/25 port was in Err-Disabled status | - | Zone 13 | 25.2892675° 51.5213447° | Inside Doha | P3 - Medium | 2026-03-28 23:35 | 2026-03-28 23:39 | 3.4667 | 2026-03-28 23:39 | 2026-03-28 23:39 | 0 | 3.4667 | Issue resolved after shut/unshut port | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
111 | Sirti-WAN-R3-Ticket-91 | NA | 2026-03-28 | IE5000-3202 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 39 | 25.26340° 51.49677° | Inside Doha | P2 - High | 2026-03-29 01:45 | 2026-03-29 01:48 | 2.65 | 2026-03-29 01:48 | 2026-03-29 01:49 | 0.58333 | 3.2333 | As per Logs, there was power interruption at schema site Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
112 | Sirti-WAN-R3-Ticket-92 | NA | 2026-03-28 | DC23-Enc101-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 51 | 25.3204° 51.470367° | Outside Doha | P2 - High | 2026-03-29 01:45 | 2026-03-29 01:47 | 2.1 | 2026-03-29 01:47 | 2026-03-29 01:51 | 3.8167 | 5.9167 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
113 | Sirti-WAN-R3-Ticket-93 | NA | 2026-03-28 | DC23-Enc102-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 32 | 25.321261° 51.473693° | Inside Doha | P2 - High | 2026-03-29 01:45 | 2026-03-29 01:47 | 2.1 | 2026-03-29 01:47 | 2026-03-29 01:51 | 3.8167 | 5.9167 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
114 | Sirti-WAN-R3-Ticket-94 | NA | 2026-03-28 | DC23-Enc104-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 51 | 25.320812° 51.469483° | Outside Doha | P2 - High | 2026-03-29 01:45 | 2026-03-29 01:47 | 2.1 | 2026-03-29 01:47 | 2026-03-29 01:51 | 3.8167 | 5.9167 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
115 | Sirti-WAN-R3-Ticket-95 | NA | 2026-03-29 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 20 | 25.30462 51.51743 | Inside Doha | P2 - High | 2026-03-29 09:25 | 2026-03-29 09:29 | 3.95 | 2026-03-29 09:29 | 2026-03-29 09:40 | 11 | 14.95 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hichem
116 | Sirti-WAN-R3-Ticket-96 | NA | 2026-03-29 | SAL-ENC09-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-29 09:40 | 2026-03-29 09:41 | 1.4833 | 2026-03-29 09:41 | 2026-03-29 09:42 | 0.71667 | 2.2 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
117 | Sirti-WAN-R3-Ticket-97 | NA | 2026-03-29 | SAL-ENC09-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-29 09:44 | 2026-03-29 09:45 | 0.96667 | 2026-03-29 09:45 | 2026-03-29 09:47 | 2.0167 | 2.9833 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
118 | Sirti-WAN-R3-Ticket-98 | NA | 2026-03-29 | SAL-ENC50-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 96 | 24.9513076° 50.9993542° | Outside Doha | P2 - High | 2026-03-29 10:51 | 2026-03-29 10:53 | 2.3333 | 2026-03-29 10:53 | 2026-03-29 10:53 | 0.25 | 2.5833 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
119 | Sirti-WAN-R3-Ticket-99 | NA | 2026-03-29 | SAL-ENC50-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | - | Zone 96 | 24.9513076° 50.9993542° | Outside Doha | P2 - High | 2026-03-29 13:41 | 2026-03-29 13:43 | 2.05 | 2026-03-29 13:43 | 2026-03-29 13:43 | 0.33333 | 2.3833 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
120 | Sirti-WAN-R3-Ticket-100 | NA | 2026-03-29 | SAL-ENC09-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found that Another contractor(prime craft) is working on the feeder pillar | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-29 13:33 | 2026-03-29 13:37 | 4 | 2026-03-29 13:37 | 2026-03-29 14:22 | 44.6833 | 48.6833 | FLM found that Another contractor(prime craft) is working on the feeder pillar | Completed | Non-maintainer | 3rd Party | Work carried out by another subcontractor | Network Back Online | Irshad
121 | Sirti-WAN-R3-Ticket-101 | NA | 2026-03-29 | SAL-ENC50-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found that Another contractor(prime craft) is working on the feeder pillar | - | Zone 96 | 24.9513076° 50.9993542° | Outside Doha | P2 - High | 2026-03-29 15:57 | 2026-03-29 15:59 | 2.3833 | 2026-03-29 15:59 | 2026-03-29 16:38 | 38.7 | 41.0833 | FLM found that Another contractor(prime craft) is working on the feeder pillar | Completed | Non-maintainer | 3rd Party | Work carried out by another subcontractor | Network Back Online | Masthanbasha
122 | Sirti-WAN-R3-Ticket-102 | NA | 2026-03-29 | SAL-ENC09-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-29 17:42 | 2026-03-29 17:44 | 1.7667 | 2026-03-29 17:44 | 2026-03-29 17:44 | 0.21667 | 1.9833 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
123 | Sirti-WAN-R3-Ticket-103 | NA | 2026-03-29 | SAL-ENC09-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found that the CB inside the feeder pillar is tripped | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-29 19:34 | 2026-03-29 19:43 | 9.45 | 2026-03-29 20:41 | 2026-03-29 21:24 | 43.05 | 110.5 | FLM switched on main CB at feeder pillar. Breaker tripped due to Kahramaa instability | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Masthanbasha
124 | Sirti-WAN-R3-Ticket-104 | NA | 2026-03-30 | SAL-ENC09-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | AC FAN faulty (Overheating) | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-30 06:57 | 2026-03-30 06:58 | 1.1667 | 2026-03-30 06:58 | 2026-03-30 06:59 | 0.85 | 2.0167 | The alarm auto restored however the FLM went to the site and replaced the fan compressor | Completed | Maintainer | N/a | N/a | Network Back Online | -
125 | Sirti-WAN-R3-Ticket-105 | NA | 2026-03-30 | RMC-ENC-SSW-01 | Sanket | Optical Invalid | High power | High power in 100GE 1/4/0/33 | - | Zone 58 | 25.2410344° 51.4752267° | Outside Doha | P3 - Medium | 2026-03-30 08:40 | 2026-03-30 08:45 | 5.5 | 2026-03-30 08:52 | 2026-03-30 09:20 | 28.3333 | 40.3333 | 5dB attenuator added in both the port of RMC-ENC-SSW-01 (100GE 1/4/0/33 and 100GE 2/4/0/33) | Completed | Maintainer | N/a | N/a | Network Back Online | Arfa
126 | Sirti-WAN-R3-Ticket-106 | NA | 2026-03-30 | SAL-ENC09-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Khahram power line cut | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-30 17:58 | 2026-03-30 18:03 | 4.7 | 2026-03-30 19:02 | 2026-03-31 01:21 | 379.1667 | 442.8667 | Khahram power line issue.khahram team is working on finding fault at power lines. Site was temporery powered up with PG. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Sanjeewa / Ghulam
127 | Sirti-WAN-R3-Ticket-107 | NA | 2026-03-30 | P007C2-ENC89-CE-01 P007C2-ENC89-CE-02 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | MCB at FP was tripped. | - | Zone 36 | 25.2960119° 51.4742727° | Inside Doha | P2 - High | 2026-03-30 20:58 | 2026-03-30 21:07 | 9.1167 | 2026-03-30 21:36 | 2026-03-30 23:26 | 109.65 | 147.7667 | MCB was tripped at FP. PG was installed during finding FP location. | Completed | Maintainer | N/a | N/a | Network Back Online | Masthanbasha
128 | Sirti-WAN-R3-Ticket-108 | NA | 2026-03-31 | IE5000-1003 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | alarm is auto clear before visiting the site | - | Zone 20 | 25.30462 51.51743 | Inside Doha | P2 - High | 2026-03-31 11:26 | 2026-03-31 11:28 | 2.2333 | 2026-03-31 11:28 | 2026-03-31 11:38 | 10.4333 | 12.6667 | alarm is auto clear before visiting the site , suspecting power is flapped | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
129 | Sirti-WAN-R3-Ticket-109 | NA | 2026-03-31 | P007C2-ENC89-CE-01 P007C2-ENC89-CE-02 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | MCB at FP was tripped. | - | Zone 36 | 25.2960119° 51.4742727° | Inside Doha | P2 - High | 2026-03-31 14:00 | 2026-03-31 14:06 | 6.4167 | 2026-03-31 14:51 | 2026-03-31 15:29 | 38 | 89.4167 | MCB was tripped at FP, FLM switch on the MCB at the FP | Completed | Maintainer | N/a | N/a | Network Back Online | Khadar basha syed
130 | Sirti-WAN-R3-Ticket-110 | NA | 2026-03-31 | SAL-ENC09-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Device was energized by generator | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-03-31 19:11 | 2026-03-31 19:13 | 2.4 | 2026-03-31 19:13 | 2026-03-31 19:20 | 7.0833 | 9.4833 | FLM disconneced the Generator and powered up the device through Kharahma supply | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Sanjeewa
131 | Sirti-WAN-R3-Ticket-111 | NA | 2026-04-01 | P028C2-ENC04-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | UPS CB is tripped when Aircondition is on |  | Zone 13 | 25.2791625° 51.5290008° | Inside Doha | P2 - High | 2026-04-01 09:10 | 2026-04-01 09:12 | 2.5 | 2026-04-01 09:12 | 2026-04-01 09:21 | 9.4833 | 11.9833 | Device auto restored however the FLM went to the site and switched on the UPS CB and switched off the Aircondition. | Completed | Maintainer | N/a | N/a | Network Back Online | hicham
132 | Sirti-WAN-R3-Ticket-112 | NA | 2026-04-01 | P008C3-ENC01-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team |  | Zone 55 | 25.2614822° 51.4801647° | Outside Doha | P2 - High | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 | According to Mr. Salman from Salam Tech, there was DC power issue in the switch at LAN Ring which was resolved after restarting switch . The fluctuation had been occurring repeatedly at intervals of 2, 4, and 5 minutes during the mentioned time frame | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
133 | Sirti-WAN-R3-Ticket-113 | NA | 2026-04-01 | P008C3-ENC04-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team |  | Zone 55 | 25.2570167° 51.4842069° | Outside Doha | P2 - High | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
134 | Sirti-WAN-R3-Ticket-114 | NA | 2026-04-01 | P008C3-ENC07-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team |  | Zone 56 | 25.2503634° 51.4854925° | Outside Doha | P2 - High | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
135 | Sirti-WAN-R3-Ticket-115 | NA | 2026-04-01 | P008C3-ENC05-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team |  | Zone 55 | 25.2565555° 51.4854834° | Outside Doha | P2 - High | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
136 | Sirti-WAN-R3-Ticket-116 | NA | 2026-04-01 | P008C3-ENC09-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team |  | Zone 56 | 25.253746° 51.4904411° | Outside Doha | P2 - High | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
137 | Sirti-WAN-R3-Ticket-117 | NA | 2026-04-01 | P008C3-ENC19-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team |  | Zone 56 | 25.2366977° 51.4964187° | Outside Doha | P2 - High | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
138 | Sirti-WAN-R3-Ticket-118 | NA | 2026-04-01 | P008C3-ENC25-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team |  | Zone 56 | 25.2341068° 51.50261° | Outside Doha | P2 - High | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
139 | Sirti-WAN-R3-Ticket-119 | NA | 2026-04-02 | P059C1-Enc42-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage |  | Zone 70 | 25.56931971° 51.41540451° | Outside Doha | P2 - High | 2026-04-02 02:51 | 2026-04-02 02:55 | 4 | 2026-04-02 02:55 | 2026-04-02 02:56 | 1 | 5 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
140 | Sirti-WAN-R3-Ticket-120 | NA | 2026-04-02 | IE5000-1003 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | - | Zone 20 | 25.30462 51.51743 | Inside Doha | P2 - High | 2026-04-02 06:38 | 2026-04-02 06:44 | 6 | 2026-04-02 06:44 | 2026-04-02 06:58 | 14 | 20 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
141 | Sirti-WAN-R3-Ticket-121 | NA | 2026-04-02 | P028C2-ENC01-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power at cabinet |  | Zone 7 | 25.283910° 51.5496128° | Inside Doha | P2 - High | 2026-04-02 09:14 | 2026-04-02 09:18 | 4.4833 | 2026-04-02 09:27 | 2026-04-02 09:35 | 7.9333 | 21.4167 | FLM switched on tripped CB at FP | Completed | Maintainer | N/a | N/a | Network Back Online | Hicham
142 | Sirti-WAN-R3-Ticket-122 | NA | 2026-04-02 | SAL-ENC20-CE-01 | AMR | Power Fault | Power Fault | UPS Battery Faulty |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2025-09-11 16:10 | 2025-09-11 16:11 | 1 | 2026-04-02 12:27 | 2026-04-02 12:59 | 32 | 292129.15 | Action: UPS restarted. Now All power modules are running stable. UPS output : 246V | Completed | Non-maintainer | N/a | TTG | Network Back Online | Hicham
143 | Sirti-WAN-R3-Ticket-123 | NA | 2026-04-02 | SAL-ENC20-CE-01 | AMR | Poower Modules Stopped Working | Poower Modules Stopped Working | UPS Battery Faulty |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-03-31 17:23 | 2026-03-31 17:24 | 0.93333 | 2026-04-02 12:27 | 2026-04-02 12:59 | 32 | 2615.9333 | Action: UPS restarted. Now All power modules are running stable. UPS output : 246V | Completed | Non-maintainer | N/a | TTG | Network Back Online | Hicham
144 | Sirti-WAN-R3-Ticket-124 | NA | 2026-04-03 | P014-ENC04-DSW04 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Fluctuation | Alarm is auto clear before visiting the site. The devices was fluctuated for 20 seconds in the interval of seven. The Schema maitained by Salam Tech |  | Zone 44 | 25.254° 51.52375° | Outside Doha | P2 - High | 2026-04-03 02:22 | 2026-04-03 02:27 | 5 | 2026-04-03 02:27 | 2026-04-03 03:11 | 44.2167 | 49.2167 | Alarm is auto clear before visiting the site. The devices was fluctuated for 20 seconds in the interval of seven. The Schema maitained by Salam Tech | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online | -
145 |  |  |  | P014-ENC07-DSW07 | [5 empty] | Zone 44 | 25.2546112° 51.5246112° | Outside Doha | P2 - High | 2026-04-03 02:21 | 2026-04-03 02:27 | 5.6833 | 2026-04-03 02:27 | 2026-04-03 03:07 | 40.2167 | 45.9
146 |  |  |  | P014-ENC10-DSW10 | [5 empty] | Zone 45 | 25.253896 51.535995 | Outside Doha | P2 - High | 2026-04-03 02:27 | 2026-04-03 02:32 | 5.0667 | 2026-04-03 02:32 | 2026-04-03 03:06 | 34.2 | 39.2667
147 |  |  |  | P014-ENC11-DSW11 | [5 empty] | Zone 45 | 25.2545833° 51.5367222° | Outside Doha | P2 - High | 2026-04-03 02:38 | 2026-04-03 02:40 | 1.5833 | 2026-04-03 02:40 | 2026-04-03 03:06 | 26.3833 | 27.9667
148 |  |  |  | P014-ENC12-DSW12 | [5 empty] | Zone 45 | 25.524911 51.54895 | Outside Doha | P2 - High | 2026-04-03 02:33 | 2026-04-03 02:40 | 7.25 | 2026-04-03 02:40 | 2026-04-03 03:06 | 26.3833 | 33.6333
149 | Sirti-WAN-R3-Ticket-125 | NA | 2026-04-03 | P015-ENC93-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage |  | Zone 90 | 25.1143801° 51.5957564° | Outside Doha | P2 - High | 2026-04-03 08:47 | 2026-04-03 08:49 | 2 | 2026-04-03 08:49 | 2026-04-03 08:49 | 0.56667 | 2.5667 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
150 | Sirti-WAN-R3-Ticket-126 | NA | 2026-04-04 | P040-CPE02-ENC21-DSW | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage |  | Zone 57 | 25.189354 51.448508 | Outside Doha | P2 - High | 2026-04-04 11:10 | 2026-04-04 11:20 | 10.0333 | 2026-04-04 11:24 | 2026-04-04 11:32 | 7.95 | 21.9833 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | Rizwan
151 | Sirti-WAN-R3-Ticket-127 | NA | 2026-04-05 | IE5000-1003 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma power fluctuation | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-05 14:32 | 2026-04-05 14:37 | 5.4 | 2026-04-05 14:32 | 2026-04-05 14:41 | 9.6333 | 9.6333 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
152 | Sirti-WAN-R3-Ticket-128 | NA | 2026-04-05 | P008C2-Enc24-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma power fluctuation |  | Zone 44 | 25.2504372° 51.5239383° | Outside Doha | P2 - High | 2026-04-05 16:18 | 2026-04-05 16:20 | 1.8667 | 2026-04-05 16:20 | 2026-04-05 16:23 | 3.2167 | 5.0833 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
153 | Sirti-WAN-R3-Ticket-129 | NA | 2026-04-05 | P008C2-Enc24-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB tripped during PPM |  | Zone 44 | 25.2504372° 51.5239383° | Outside Doha | P2 - High | 2026-04-05 17:09 | 2026-04-05 17:12 | 3.4167 | 2026-04-05 17:12 | 2026-04-05 17:14 | 1.8667 | 5.2833 | Device went down due to ongoing PPM activity by FLM | Completed | Non-maintainer | Scheduled Works | PPM | Network Back Online | -
154 | Sirti-WAN-R3-Ticket-130 | NA | 2026-04-06 | IE5000-3903 | Sanket/Abu baker | Communication betweeen NMS and NE is Abnormal | Device Down | Power was OK at site while device is down |  | Zone 39 | 25.263350 51.496886 | Inside Doha | P2 - High | 2026-04-06 05:43 | 2026-04-06 05:53 | 9.7333 | 2026-04-06 06:33 | 2026-04-06 07:21 | 47.9167 | 97.65 | Device restored after changing the power from PS1 to PS2 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hicham
155 | Sirti-WAN-R3-Ticket-131 | NA | 2026-04-07 | IE5000-1003 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Alarm is auto cleared before FLM visiting the site. As per logs it is related to power instability. IE5000-1702, IE5000-3101 & IE5000-6009 was flapped for around 40 Sec (Ring conversion time) | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-07 07:44 | 2026-04-07 07:48 | 3.6167 | 2026-04-07 07:44 | 2026-04-07 07:50 | 6 | 6 | Device Auto restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
156 | Sirti-WAN-R3-Ticket-132 | NA | 2026-04-07 | IE5000-1003 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma power fluctuation | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-07 09:47 | 2026-04-07 09:50 | 2.5833 | 2026-04-07 09:47 | 2026-04-07 09:56 | 8.6667 | 8.6667 | FLM team was on site during incident, observed power interruption caused the device to be down | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Najeeb
157 | Sirti-WAN-R3-Ticket-133 | NA | 2026-04-08 | IE5000-1003 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-08 05:40 | 2026-04-08 05:43 | 3 | 2026-04-08 06:29 | 2026-04-08 07:49 | 79.8167 | 128.7333 | Device was down due to power outage | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Kwadwo
158 | Sirti-WAN-R3-Ticket-134 | NA | 2026-04-08 | IE5000-1003 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-08 08:06 | 2026-04-08 08:09 | 2.5333 | 2026-04-08 08:06 | 2026-04-08 08:56 | 49.6833 | 49.6833 | Device was down due to power outage | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
159 | Sirti-WAN-R3-Ticket-135 | NA | 2026-04-08 | P015-ENC22B-UPE-02 P015-ENC24A-CE-01 P015-SS1-USG-02 P015-ENC19A-CE-01 P015-ENC80A-CE-01 P015-SS1-CE-01 P015-ENC18-CE-01 P015-ENC22A-CE-01 P015-ENC22B-CE-01 P015-ENC56-CE-01 P015-ENC93-CE-01 P015-SS1-USG-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | - | Zone 90 | 25.131934° 51.5866756° | Outside Doha | P1 - Critical | 2026-04-08 07:11 | 2026-04-08 07:22 | 10.8333 | 2026-04-08 08:10 | 2026-04-08 13:51 | 341.3167 | 400.15 | Devices were down due to Kharahma major outage -Lockk down in multiple sites which affected multiple nodes as well as the ring protection There was no Kharahma power at the following: P015-ENC22B-UPE-02 P015-ENC24A-CE-01 P015-ENC19A-CE-01 P015-ENC18-CE-01 P015-ENC22A-CE-01 P015-ENC22B-CE-01 P015-ENC56-CE-01 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Najeeb / Hicham
160 | Sirti-WAN-R3-Ticket-136 | NA | 2026-04-09 | IE5000-1003 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-09 06:21 | 2026-04-09 06:23 | 1.65 | 2026-04-09 06:57 | 2026-04-09 07:28 | 31.5667 | 67.1 | Device was down due to KHARAMAA issue. Temporary genertaor is connected to resolved the issue. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Irshad
161 | Sirti-WAN-R3-Ticket-137 | NA | 2026-04-09 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-09 12:08 | 2026-04-09 12:12 | 3.35 | 2026-04-09 12:18 | 2026-04-09 12:26 | 7.35 | 17.35 | Due to Kharahma power, the device was running on generator.Suddenly the circuit breaker tripped and the device shut down. Later, the circuit breaker was turned ON again. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Irshad
162 | Sirti-WAN-R3-Ticket-138 | NA | 2026-04-09 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-09 13:00 | 2026-04-09 13:04 | 4 | 2026-04-09 13:10 | 2026-04-09 13:16 | 5.7167 | 15.7167 | We removed the generator and started the device on Kahramaa | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Irshad
163 | Sirti-WAN-R3-Ticket-139 | NA | 2026-04-09 | IE5000-1003 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | device down flapped for 5 min and auto-restored | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-09 16:11 | 2026-04-09 16:13 | 2 | 2026-04-09 16:11 | 2026-04-09 16:16 | 5 | 5 | device down flapped for 5 min and auto-restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
164 | Sirti-WAN-R3-Ticket-140 | NA | 2026-04-10 | P023C1-ENC01-UPE-01 | Abubaker | Link Down (100GE 1/0/1) | 100GE Link Down | Link Down (100GE 1/0/1) due to QNBN Planned Activity | - | Zone 90 | 25.111748° 51.583897° | Outside Doha | P3 - Medium | 2026-04-10 01:01 | 2026-04-10 01:06 | 5 | 2026-04-10 01:18 | 2026-04-10 03:20 | 122 | 139 | Planned activity by QNBN (Ref # PWA-RMD-0104) | Completed | Non-maintainer | 3rd Party | QNBN | Link is up and alarm cleared | -
165 | Sirti-WAN-R3-Ticket-141 | NA | 2026-04-10 | IE5000-1003 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Traffic Signal Contractor Activity | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-10 04:26 | 2026-04-10 04:34 | 8 | 2026-04-10 04:34 | 2026-04-10 04:51 | 17 | 25 | Device went down due to TS contractor activity, the switched off the CB. | Completed | Non-maintainer | 3rd Party | TS contractor | Network Back Online | Ghulam
166 | Sirti-WAN-R3-Ticket-142 | NA | 2026-04-10 | IE5000-1003 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KTC team turned off Breaker at FP for their activity | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-10 07:15 | 2026-04-10 07:18 | 3 | 2026-04-10 07:18 | 2026-04-10 07:24 | 6 | 9 | Device went down due to TS contractor activity, the switched off the CB. | Completed | Non-maintainer | 3rd Party | TS contractor | Network Back Online | Ghulam
167 | Sirti-WAN-R3-Ticket-143 | NA | 2026-04-10 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Traffic Signal Contractoris working | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-10 19:40 | 2026-04-10 19:42 | 2 | 2026-04-10 19:42 | 2026-04-10 20:40 | 58 | 60 | No power in the cabinet. Tripped off main ITS-FP- breaker | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Eric
168 | Sirti-WAN-R3-Ticket-144 | NA | 2026-04-11 | P059C1-Enc04-UPE-01 P059C1-Enc04-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | Kharahma Outage |  | Zone 71 | 25.3653937° 51.4467471° | Outside Doha | P2 - High | 2026-04-11 08:47 | 2026-04-11 08:50 | 3.1333 | 2026-04-11 10:09 | 2026-04-11 10:50 | 40.85 | 123.3333 | Khahrama outage. Device was temoprery powered up with DG . Later discnnected on khahrama restoration | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Rizwan
169 | Sirti-WAN-R3-Ticket-145 | NA | 2026-04-12 | RAA-ENC24-UPE-02 RAA-ENC24-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | - | Zone 49 | 25.23647° 51.58650° | Outside Doha | P2 - High | 2026-04-12 03:17 | 2026-04-12 03:20 | 3.4167 | 2026-04-12 03:17 | 2026-04-12 03:57 | 40.35 | 40.35 | As per the logs indicating a power interruption.Devices auto Restored before FLM reached the site. | Completed | Maintainer | N/a | N/a | Network Back Online | Ghulam / SARJOON
170 | Sirti-WAN-R3-Ticket-146 | NA | 2026-04-12 | P002-ENC13-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB tripped at FP end |  | Zone 58 | 25.248 51.47325 | Outside Doha | P2 - High | 2026-04-12 07:24 | 2026-04-12 07:28 | 4.3333 | 2026-04-12 08:08 | 2026-04-12 08:37 | 29.35 | 73.2 | CB tripped at FP side. Site restored after turning on CB | Completed | Maintainer | N/a | N/a | Network Back Online | Rizwan
171 | Sirti-WAN-R3-Ticket-147 | NA | 2026-04-12 | RAA-Enc24-UPE-01 RAA-Enc24-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | 3rd party team was working at FP for their activity |  | Zone 49 | 25.23647° 51.58650° | Outside Doha | P2 - High | 2026-04-12 09:49 | 2026-04-12 09:54 | 4.55 | 2026-04-12 09:54 | 2026-04-12 10:07 | 13.1167 | 17.6667 | Upon FLM arrival, team found 3rd party contractor was working at FP. Device restored after khahrama restored from FP side. | Completed | Non-maintainer | 3rd Party | Another Sub Contractor | Network Back Online | Hichem
172 | Sirti-WAN-R3-Ticket-148 | NA | 2026-04-12 | P011-Enc55-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. |  | Zone 49 | 25.2209722° 51.5862222° | Outside Doha | P2 - High | 2026-04-12 11:53 | 2026-04-12 11:56 | 3.0833 | 2026-04-12 11:56 | 2026-04-12 11:58 | 2.0333 | 5.1167 | As per the logs indicating a power interruption.Devices auto Restored before FLM reached the site. | Completed | Maintainer | N/a | N/a | Network Back Online | -
173 | Sirti-WAN-R3-Ticket-149 | NA | 2026-04-12 | P012-Enc97-UPE-02 | Aaqib | Power Modules stopped working | Pwr3 & Pwr4 Modules Stopped Working | Routine PPM by P012 Tunnel team |  | Zone 56 | 25.1926322 51.4542203 | Outside Doha | P3 - Medium | 2026-04-12 11:53 | 2026-04-12 11:58 | 5.3833 | 2026-04-12 11:58 | 2026-04-12 12:15 | 17.25 | 22.6333 | As per tunnel team, 1 Source is down due ongoing PPM activity. Modules are powered up and under observation. | Completed | Maintainer | N/a | N/a | Network Back Online | -
174 | Sirti-WAN-R3-Ticket-150 | NA | 2026-04-12 | P006-Enc17-UPE-02 P006-Enc17-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-04-12 12:28 | 2026-04-12 12:30 | 1.8833 | 2026-04-12 12:30 | 2026-04-12 12:35 | 4.8333 | 6.7167 | Device rebooted during UPS testing activity. | Completed | Maintainer | N/a | N/a | Network Back Online | -
175 | Sirti-WAN-R3-Ticket-151 | NA | 2026-04-13 | P012-ENC16-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | CB tripped at FP end | - | Zone 56 | 25.2250231° 51.5095445° | Outside Doha | P2 - High | 2026-04-13 09:55 | 2026-04-13 10:04 | 9 | 2026-04-13 11:14 | 2026-04-13 11:38 | 23.65 | 103 | no power in the cabinet. Tripped off main ITS-FP- breaker | Completed | Maintainer | N/a | N/a | Network Back Online | Najeeb
176 | Sirti-WAN-R3-Ticket-152 | NA | 2026-04-13 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-13 08:26 | 2026-04-13 08:30 | 4.1667 | 2026-04-13 08:30 | 2026-04-13 08:32 | 2.3 | 6.4667 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
177 | Sirti-WAN-R3-Ticket-153 | NA | 2026-04-13 | P005-ENC401-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The UPS has input power, but there is no output power in FP |  | Zone 52 | 25.31049° 51.45271° | Outside Doha | P2 - High | 2026-04-13 11:28 | 2026-04-13 11:30 | 2.1833 | 2026-04-13 12:50 | 2026-04-13 14:00 | 69.6833 | 151.95 | Power is available on the Kharama side and is connected to the UPS. The UPS has input power, but there is no output power. We will connect the Kahramaa power directly to the cabinet. | Completed | Non-Maintainer | N/a | N/a | Network Back Online | Irshad
178 | Sirti-WAN-R3-Ticket-154 | NA | 2026-04-13 | DUK-ENC12-CE-01 | Sanket | Optical module Temperature too High | High Temperature | alarm is auto clear before visiting the site | - | Zone 72 | 25.4322949° 51.1106559° | Outside Doha | P3 - Medium | 2026-04-13 12:35 | 2026-04-13 12:44 | 9 | 2026-04-13 12:44 | 2026-04-13 13:40 | 55.6833 | 64.6833 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online | -
179 | Sirti-WAN-R3-Ticket-155 | NA | 2026-04-14 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-14 09:40 | 2026-04-14 09:43 | 3 | 2026-04-14 09:43 | 2026-04-14 09:56 | 13.6667 | 16.6667 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
180 | Sirti-WAN-R3-Ticket-156 | NA | 2026-04-14 | P005-ENC401-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The UPS has input power, but there is no output from the UPS, | - | Zone 52 | 25.31049° 51.45271° | Outside Doha | P2 - High | 2026-04-14 10:21 | 2026-04-14 10:23 | 1.35 | 2026-04-14 10:26 | 2026-04-14 10:43 | 17.4167 | 21.7667 | Power is available from the Kahramaa side, and the UPS has incoming supply.There is no output from the UPS, and the display is not functioning. The cabinet was temporarily connected directly to Kahramaa power by Irshad’s team yesterday. After checking incoming power to the UPS is confirmed, but there is still no display and no output. The issue is suspected to be with the UPS itself, not the batteries | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online | Najeeb
181 | Sirti-WAN-R3-Ticket-157 | NA | 2026-04-14 | P040-CPE02-ENC21-DSW | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | UPS CB Tripped | - | Zone 57 | 25.189354 51.448508 | Outside Doha | P2 - High | 2026-04-14 09:42 | 2026-04-14 09:45 | 3.1833 | 2026-04-14 10:25 | 2026-04-14 11:18 | 53.1667 | 96.35 | UPS input circuit breaker tripped. The schema maintained by ITSQ | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Network Back Online | Patrick
182 | Sirti-WAN-R3-Ticket-158 | NA | 2026-04-14 | P040-CPE02-ENC21-DSW | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | UPS CB Tripped | - | Zone 57 | 25.189354 51.448508 | Outside Doha | P2 - High | 2026-04-14 11:22 | 2026-04-14 11:24 | 2 | 2026-04-14 11:27 | 2026-04-14 11:34 | 7.4833 | 12.4833 | The ITSQ team bypass the UPS and directely connect the Kharamaa | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Network Back Online | Patrick
183 | Sirti-WAN-R3-Ticket-159 | NA | 2026-04-16 | P012-ENC17-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption (alarm is auto clear before visiting the site) | - | Zone 56 | 25.2323137° 51.5085231° | Outside Doha | P2 - High | 2026-04-16 07:32 | 2026-04-16 07:36 | 4 | 2026-04-16 07:36 | 2026-04-16 07:37 | 0.78333 | 4.7833 | As per the LOGS, device is rebooted (Power Interruption) | Completed | Maintainer | N/a | N/a | Devices Back Online | -
184 | Sirti-WAN-R3-Ticket-160 | NA | 2026-04-16 | P012-ENC33-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption (alarm is auto clear before visiting the site) | - | Zone 56 | 25.2282194° 51.5019836° | Outside Doha | P2 - High | 2026-04-16 08:37 | 2026-04-16 08:40 | 3 | 2026-04-16 08:40 | 2026-04-16 08:44 | 3.6 | 6.6 | As per the LOGS, device is rebooted (Power Interruption) | Completed | Maintainer | N/a | N/a | Devices Back Online | -
185 | Sirti-WAN-R3-Ticket-161 | NA | 2026-04-16 | P002-ENC01-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption (alarm is auto clear before visiting the site) | - | Zone 55 | 25.2632875° 51.4952573° | Outside Doha | P2 - High | 2026-04-16 14:17 | 2026-04-16 14:23 | 5.75 | 2026-04-16 14:23 | 2026-04-16 14:26 | 3 | 8.75 | As per the LOGS, device is rebooted (Power Interruption) | Completed | Maintainer | N/a | N/a | Devices Back Online | -
186 | Sirti-WAN-R3-Ticket-162 | NA | 2026-04-16 | P002-ENC01-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | There was a switch-off at the rectifier site on UPS 3 and UPS 4. After switching them back on, the node was powered up |  | Zone 55 | 25.2632875° 51.4952573° | Outside Doha | P2 - High | 2026-04-16 14:59 | 2026-04-16 15:01 | 2.05 | 2026-04-16 15:01 | 2026-04-16 15:07 | 6.2 | 8.25 | All four UPS units and battery sets were checked for input and output voltage, and UPS units are reset and monitored for a few hours; the node operated continuously without failure | Completed | Non-maintainer | 3rd Party | RMC | Devices Back Online | -
187 | Sirti-WAN-R3-Ticket-163 | NA | 2026-04-16 | P002-ENC01-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | - No power on cabinet - UPS3 and UPS4 CBs were tripped - UPS1 and UPS2 are in fault mode |  | Zone 55 | 25.2632875° 51.4952573° | Outside Doha | P2 - High | 2026-04-16 15:18 | 2026-04-16 15:22 | 4.25 | 2026-04-16 15:55 | 2026-04-16 16:13 | 18.1833 | 55.4333 | - FLM found no power on the cabinet as the UPS CB tripped. - Device restored after switching ON the UPS CB. - Restarted the UPS1 and UPS2 and cleared the fault | Completed | Non-maintainer | 3rd Party | RMC | Devices Back Online | Sanjeewa
188 | Sirti-WAN-R3-Ticket-164 | NA | 2026-04-17 | IE5000-1003 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Main CB Tripped | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-17 14:22 | 2026-04-17 14:25 | 3.1667 | 2026-04-17 14:53 | 2026-04-17 14:59 | 5.7333 | 36.8167 | The circuit breaker in the cabinet has tripped. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Eric
189 | Sirti-WAN-R3-Ticket-165 | NA | 2026-04-18 | P023C1-ENC01-UPE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC compressor is faulty and needs replacement. Additionally, the system requires a gas refill and a complete servicing | - | Zone 90 | 25.111748° 51.583897° | Outside Doha | P3 - Medium | 2026-04-18 09:53 | 2026-04-18 09:59 | 5.7333 | 2026-04-18 10:40 | 2026-04-18 10:50 | 9.7667 | 57.0167 | FLM isited the site and checked dual A/C system in WAN cabinet. AC1: Gas leakage found at pin valve → replaced valve, refilled gas, cleaned unit → tested OK (cooling normal). AC2: Compressor found faulty → replaced compressor (SECOP SC15G), refilled gas, cleaned unit → tested OK (cooling normal). Both A/C units are now operational and cooling properly. | Completed | Maintainer | N/a | N/a | Alarm Cleared | Eric
190 | Sirti-WAN-R3-Ticket-166 | NA | 2026-04-18 | P060-ENC179-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC compressor is faulty and needs replacement. Additionally, the system requires a gas refill and a complete servicing |  | Zone 70 | 25.639484° 51.491537° | Outside Doha | P3 - Medium | 2026-04-18 14:41 | 2026-04-18 14:44 | 3.65 | 2026-04-18 15:20 | 2026-04-18 15:29 | 8.1833 | 47.8333 | FLM visited the site and checked dual A/C system in WAN cabinet. AC1: Gas leakage found at pin valve → replaced valve, refilled R134a gas, cleaned unit → tested OK (cooling normal). AC2: Compressor missing → installed new compressor (SECOP SC15G), refilled R134a gas, cleaned unit → tested OK (cooling normal). Both A/C units are now operational and cooling properly. | Completed | Maintainer | N/a | N/a | Alarm Cleared | Eric
191 | Sirti-WAN-R3-Ticket-167 | NA | 2026-04-18 | P004- TMC-NPE and P004_DWDM | Sanket | Power Modules stopped working | Power module powered off | KAHRAMAA power interruption. | - | Zone 51 | 25.319385 51.352255 | Outside Doha | P3 - Medium | 2026-04-18 19:21 | 2026-04-18 19:26 | 5.5833 | 2026-04-18 20:13 | 2026-04-18 20:33 | 19.4167 | 71.7333 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Sanjeewa
192 | Sirti-WAN-R3-Ticket-168 | NA | 2026-04-18 | IE5000-1003 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | RCCB CB Tripped | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-18 23:43 | 2026-04-18 23:45 | 1.6167 | 2026-04-19 00:35 | 2026-04-19 00:53 | 18.3833 | 70 | The circuit breaker in the cabinet has tripped due to unstable power. FLM switched on the RCCB. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Ghulam
193 | Sirti-WAN-R3-Ticket-169 | NA | 2026-04-19 | DUK-ENC06-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | GE1/0/9 toward Local Node was down | - | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | P2 - High | 2026-04-19 00:31 | 2026-04-19 00:38 | 7.4667 | 2026-04-19 00:31 | 2026-04-19 01:08 | 37.3 | 37.3 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Port is up and alarm cleared
194 | Sirti-WAN-R3-Ticket-170 | NA | 2026-04-19 | IE5000-1003 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity by FLM to check and verify the power cable from service cabinet to IE5000-1003 enclosure | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-19 01:47 | 2026-04-19 01:49 | 2.1167 | 2026-04-19 01:47 | 2026-04-19 01:54 | 7.3333 | 7.3333 | Checked and reconnected the power cable inside the IE5000-1003 service cabinet | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Ghulam
195 | Sirti-WAN-R3-Ticket-171 | NA | 2026-04-19 | IE5000-1003 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity by FLM to check and verify the power cable inside IE5000-1003 enclosure | - | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-19 02:54 | 2026-04-19 03:03 | 8.6167 | 2026-04-19 02:54 | 2026-04-19 03:19 | 24.2167 | 24.2167 | Checked and reconnected the power cable inside the IE5000-1003 Enclosure | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Ghulam
196 | Sirti-WAN-R3-Ticket-172 | NA | 2026-04-19 | IE5000-1003 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. |  | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-19 08:57 | 2026-04-19 08:59 | 1.4833 | 2026-04-19 08:57 | 2026-04-19 09:00 | 3.3 | 3.3 | As per the LOGS, device is rebooted (Power Interruption) | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
197 | Sirti-WAN-R3-Ticket-173 | NA | 2026-04-19 | IE5000-1003 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Power interruption due to CB Tripping |  | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-19 09:10 | 2026-04-19 09:11 | 0.78333 | 2026-04-19 09:10 | 2026-04-19 09:15 | 4.3833 | 4.3833 | Reconnect the AC directly to the incoming power supply (instead of through the ELCB) to prevent the node from going down due to AC short faults | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
198 | Sirti-WAN-R3-Ticket-174 | NA | 2026-04-19 | P010-Enc01-CE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC compressor is faulty and needs replacement. Additionally, the system requires a gas refill and a complete servicing |  | Zone 81 | 25.139881, 51.407393 | Outside Doha | P3 - Medium | 2026-04-19 09:20 | 2026-04-19 09:23 | 2.9167 | 2026-04-19 10:51 | 2026-04-19 10:54 | 2.7833 | 93.6 | Faulty compressor was replaced with a new LG GJS222PMA model (220–250V, 50Hz, 1PH LRA42.5), along with a new 35 MFD capacitor and copper dry filter. The condenser and compressor were cleaned using nitrogen gas, R22 refrigerant was filled, and the thermostat temperature was set. All AC parts were thoroughly cleaned with a blower and towels, and after testing, the unit was observed to be cooling effectively and operating in good condition | Completed | Maintainer | N/a | N/a | Alarm Cleared | Rizwan
199 | Sirti-WAN-R3-Ticket-175 | NA | 2026-04-19 | P028C2-ENC-07-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | main CB is tripped at cabinet side |  | Zone 6 | 25.2827572° 51.5448455° | Inside Doha | P2 - High | 2026-04-19 19:24 | 2026-04-19 19:25 | 1.25 | 2026-04-19 20:08 | 2026-04-19 20:18 | 10.45 | 54.7 | FLM switched on tripped main CB at cabinet side | Completed | Maintainer | N/a | N/a | Alarm Cleared | Hassan
200 | Sirti-WAN-R3-Ticket-176 | NA | 2026-04-19 | DUK-ENC30-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | device down flapped for 2 min and auto-restored |  | Zone 85 | 25.4637854° 50.930279° | Outside Doha | P2 - High | 2026-04-19 19:35 | 2026-04-19 19:37 | 2.25 | 2026-04-19 19:37 | 2026-04-19 19:37 | 0.25 | 2.5 | device auto restored after 2 min | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
201 | Sirti-WAN-R3-Ticket-177 | NA | 2026-04-19 | P010-ENC01-CE-01 P010-ENC01-UPE01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | devices wend down while team is working for fixing faulty AC |  | Zone 81 | 25.139881, 51.407393 | Outside Doha | P2 - High | 2026-04-19 21:40 | 2026-04-19 21:42 | 2.1833 | 2026-04-19 21:43 | 2026-04-19 21:47 | 3.5833 | 6.7667 | devices wend down while team is working for fixing faulty AC | Completed | Maintainer | N/a | N/a | Alarm Cleared | Eric
202 | Sirti-WAN-R3-Ticket-178 | NA | 2026-04-19 | IE5000-1003.ashghal | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | device down flapped for 10 min and auto-restored |  | Zone 60 | 25.30450151 51.51807558 | Outside Doha | P2 - High | 2026-04-19 23:39 | 2026-04-19 23:42 | 2.7167 | 2026-04-19 23:42 | 2026-04-19 23:49 | 7.1 | 9.8167 | device down flapped for 10 min and auto-restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
203 | Sirti-WAN-R3-Ticket-179 | NA | 2026-04-20 | P010-ENC01-CE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC functioning system is not working properly |  | Zone 81 | 25.139881, 51.407393 | Outside Doha | P3 - Medium | 2026-04-20 10:47 | 2026-04-20 10:51 | 3.75 | 2026-04-20 10:59 | 2026-04-20 11:49 | 50.05 | 61.8 | FLM checked and found the AC condenser and evaporator were blocked. FLM cleaned and flushed them using 141B liquid, then dried them with nitrogen gas and a vacuum pump. After reinstalling, we refilled with R22 gas and set the temperature. Finally, we cleaned all AC parts with a blower | Completed | Non-maintainer | Defect | Fixing of Defect | Alarm Cleared | Khadar
204 | Sirti-WAN-R3-Ticket-180 | NA | 2026-04-20 | SAL-ENC09-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Polaris team is working on site changing power cable |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-04-20 15:13 | 2026-04-20 15:16 | 3.2833 | 2026-04-20 15:21 | 2026-04-20 15:38 | 17.2333 | 25.5167 | FLM reach the site and found Polaris team is working on site for changing power cable | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Devices Back Online | masthan
205 | Sirti-WAN-R3-Ticket-181 | NA | 2026-04-20 | DUK-ENC12-CE-01 | Abubaker | Link Down (GE1/0/9 toward the local device) | LAN Link Down | Port Auto restored before FLM reach the site |  | Zone 72 | 25.4322949° 51.1106559° | Outside Doha | P3 - Medium | 2026-04-20 23:10 | 2026-04-20 23:17 | 6.6167 | 2026-04-20 23:17 | 2026-04-20 23:34 | 16.55 | 23.1667 | Port GE1/0/9 flapped during the incident and Auto restored before FLM reach to the site | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
206 | Sirti-WAN-R3-Ticket-182 | NA | 2026-04-21 | DUK-ENC16-CE-01 | Abubaker | Link Down (GE1/0/9 toward the local device) | LAN Link Down | Port Auto restored before FLM reach the site |  | Zone 80 | 25.432295, 51.110656 | Outside Doha | P3 - Medium | 2026-04-21 00:46 | 2026-04-21 00:55 | 9.3333 | 2026-04-21 00:55 | 2026-04-21 01:20 | 24.9667 | 34.3 | Port GE1/0/9 flapped during the incident and Auto restored before FLM reach to the site | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
207 | Sirti-WAN-R3-Ticket-183 | NA | 2026-04-21 | P012-ENC12-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | - | Zone 56 | 25.2212138° 51.5169228° | Outside Doha | P2 - High | 2026-04-21 09:55 | 2026-04-21 09:56 | 1 | 2026-04-21 09:56 | 2026-04-21 09:59 | 3.1333 | 4.1333 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
208 | Sirti-WAN-R3-Ticket-184 | NA | 2026-04-21 | P012-ENC12-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | - | Zone 56 | 25.2212138° 51.5169228° | Outside Doha | P2 - High | 2026-04-21 10:57 | 2026-04-21 10:59 | 2 | 2026-04-21 11:45 | 2026-04-21 11:47 | 1.75 | 49.75 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
209 | Sirti-WAN-R3-Ticket-185 | NA | 2026-04-22 | P012-ENC12-CE-01 | Sanket | Link Down | LAN Link Down | GE 1/13 down towards 16041-P12-BSW | - | Zone 56 | 25.2212138° 51.5169228° | Outside Doha | P3 - Medium | 2026-04-22 06:20 | 2026-04-22 06:34 | 14 | 2026-04-22 07:10 | 2026-04-22 07:41 | 30.95 | 80.95 | The Link is down towards LAN | Completed | Maintainer | N/a | N/a | Alarm Cleared | Najeeb
210 | Sirti-WAN-R3-Ticket-185 | NA | 2026-04-22 | P012-ENC12-CE-01 | Sanket | Link Down | WAN Link Down | Port TE 1/28 towards P012-ENC09-UPE-01 port 40GE 4/0/1 is down | - | Zone 56 | 25.2212138° 51.5169228° | Outside Doha | P3 - Medium | 2026-04-22 06:20 | 2026-04-22 06:34 | 14 | 2026-04-22 07:10 | 2026-04-22 07:41 | 30.95 | 80.95 | Fiber Patch chord raplaced | Completed | Maintainer | N/a | N/a | Alarm Cleared | Najeeb
211 | Sirti-WAN-R3-Ticket-186 | NA | 2026-04-22 | P040-CPE01-ENC01-DSW | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | - | Zone 81 | 25.179715 51.408779 | Outside Doha | P2 - High | 2026-04-22 13:16 | 2026-04-22 13:18 | 1.45 | 2026-04-22 13:18 | 2026-04-22 13:20 | 2.0333 | 3.4833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Devices Back Online | -
212 | Sirti-WAN-R3-Ticket-187 | NA | 2026-04-22 | Duk-Enc34-CE-01 | Aaqib | Link Down | LAN Link Down | Port GE 1/0/9 connected towards Enc34-Local-Node went down |  | Zone 72 | 25.4537767 50.8835078 | Outside Doha | P3 - Medium | 2026-04-22 22:18 | 2026-04-22 22:20 | 2 | 2026-04-22 22:45 | 2026-04-22 22:49 | 4 | 31 | FLM checked ethernet and POE connections for the camera and found all connections are normally fixed ,suspected weather condition | Completed | Non-maintainer | Environmental | High wind Event | Alarm Cleared | farouk
213 | Sirti-WAN-R3-Ticket-188 | NA | 2026-04-23 | SAL-ENC32-CE-01 | Adel | Power Modules stopped working | Power module powered off | no abnormal observations on site | - | Zone 82 | 25.1165799° 51.1812367° | Outside Doha | P3 - Medium | 2026-04-23 21:48 | 2026-04-23 21:54 | 6 | 2026-04-23 21:54 | 2026-04-23 22:44 | 50 | 56 | Alarm is auto clear before reaching the site , FLM visited and checked all power connections and found all connections are normally connected | Completed | Maintainer | N/a | N/a | Alarm Cleared | umair
214 | Sirti-WAN-R3-Ticket-189 | NA | 2026-04-25 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. |  | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-25 08:24 | 2026-04-25 08:25 | 1 | 2026-04-25 08:25 | 2026-04-25 08:27 | 1.9833 | 2.9833 | Kahramaa planned shutdown | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
215 | Sirti-WAN-R3-Ticket-190 | NA | 2026-04-25 | SAL-ENC63-CE-01 | Sanket | Link Down | LAN Link Down | Team found no power in cabinet | - | Zone 96 | 24.8301249° , 50.8705931° | Outside Doha | P3 - Medium | 2026-04-25 13:09 | 2026-04-25 13:12 | 3 | 2026-04-25 13:58 | 2026-04-25 16:15 | 137.4667 | 186.3167 | LAN cabinet main breaker tripped due to street light CB fault; devices restored after Cabinet breaker reset | Completed | Maintainer | N/a | N/a | Alarm Cleared | Khadar
216 | Sirti-WAN-R3-Ticket-191 | NA | 2026-04-25 | P003-ENC40-UPE-02 | Sanket | Link Down | WAN Link Down | FLM found fiber cable was burnt inside the ITS chamber, with the fault located about 390 meters from JN-6401. The suspected cause is a fire originating from an advertisement board installed above the chamber, which resulted in damage to the PWA fiber cable. |  | Zone 65 | 25.3344995° 51.5180512° | Outside Doha | P3 - Medium | 2026-04-25 13:07 | 2026-04-25 13:13 | 5.75 | 2026-04-25 14:33 | 2026-04-28 00:02 | 3449.1667 | 3534.5833 | installed new fiber cable & Spliced 24 core in enclosure chamber 11 and JN-6401 | Completed | Non-maintainer | 3rd Party | Fire | Alarm Cleared | Najeeb
217 | Sirti-WAN-R3-Ticket-192 | NA | 2026-04-25 | P005-TCR-CE-02 | Aaqib | Link Down | LAN Link Down | 1x10G Link (TE 1/0/10) went down and auto restored |  | Zone 51 | 25.3199307 51.447548 | Outside Doha | P3 - Medium | 2026-04-25 17:04 | 2026-04-25 17:07 | 3 | 2026-04-25 17:07 | 2026-04-25 17:10 | 2.8 | 5.8 | Link auto restored after 5min. | Completed | Non-maintainer | 3rd Party | GBDG Contractor | Alarm Cleared | -
218 | Sirti-WAN-R3-Ticket-193 | NA | 2026-04-25 | P059C1-N3-Enc20-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 70 | 25.44194931° 51.41112813° | Outside Doha | P2 - High | 2026-04-25 18:41 | 2026-04-25 18:44 | 2.55 | 2026-04-25 18:44 | 2026-04-25 18:47 | 3.4 | 5.95 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
219 | Sirti-WAN-R3-Ticket-194 | NA | 2026-04-26 | DUK-ENC12-CE-01 | Aaqib | Link Down | LAN Link Down | Team found no power in cabinet |  | Zone 72 | 25.4322949° 51.1106559° | Outside Doha | P3 - Medium | 2026-04-26 08:01 | 2026-04-26 08:04 | 2.8667 | 2026-04-26 08:50 | 2026-04-26 10:12 | 81.4167 | 130.0833 | Planned activity by kahrama for transformer replacement at FP | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Rizwan
220 | Sirti-WAN-R3-Ticket-195 | NA | 2026-04-26 | P023C3-ENC174-UPE-02 P023C3-ENC174-CE-02 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 94 | 25.01688 , 51.49047 | Outside Doha | P2 - High | 2026-04-26 12:33 | 2026-04-26 12:35 | 2.35 | 2026-04-26 12:35 | 2026-04-26 12:38 | 2.6833 | 5.0333 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
221 | Sirti-WAN-R3-Ticket-196 | NA | 2026-04-26 | SAL-ENC63-CE-01 | Aaqib | Link Down | LAN Link Down | KAHRAMAA power interruption |  | Zone 96 | 24.8301249° , 50.8705931° | Outside Doha | P3 - Medium | 2026-04-26 12:37 | 2026-04-26 12:42 | 4.5333 | 2026-04-26 12:42 | 2026-04-26 12:49 | 7.4167 | 11.95 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
222 | Sirti-WAN-R3-Ticket-197 | NA | 2026-04-26 | P010-ENC61-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | PLanned activity for UPS battery replacment |  | Zone 81 | 25.139881, 51.407393 | Outside Doha | P2 - High | 2026-04-26 23:26 | 2026-04-26 23:27 | 0.9 | 2026-04-26 23:27 | 2026-04-27 00:30 | 63.0167 | 63.9167 | UPS batteries replacement activity was successfully completed | Completed | Non-maintainer | Planned Activity | UPS defect also | Alarm Cleared | Farooq
223 | Sirti-WAN-R3-Ticket-198 | NA | 2026-04-27 | P007C2-170018-R2-CSW | Adel | Link Down | LAN Link Down | corevit company team is performing activity at SOC P007 |  | Zone 52 | 25.2942202 51.4657002 | Outside Doha | P3 - Medium | 2026-04-27 00:19 | 2026-04-27 00:23 | 3.8333 | 2026-04-27 01:18 | 2026-04-27 02:17 | 59 | 117.8333 | multiple ports are flapped due to corevit company activity at control room | Completed | Non-maintainer | 3rd Party | corevit contractor | Alarm Cleared | umair
224 | Sirti-WAN-R3-Ticket-199 | NA | 2026-04-27 | SAL-ENC63-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 96 | 24.8301249° , 50.8705931° | Outside Doha | P2 - High | 2026-04-27 07:09 | 2026-04-27 07:12 | 2.6 | 2026-04-27 07:12 | 2026-04-27 07:14 | 2.5167 | 5.1167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
225 | Sirti-WAN-R3-Ticket-200 | NA | 2026-04-27 | P059C1-ENC23-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC CB was tripped |  | Zone 71 | 25.4516333° 51.4090805° | Outside Doha | P3 - Medium | 2026-04-27 12:41 | 2026-04-27 12:50 | 9.2167 | 2026-04-27 13:52 | 2026-04-27 14:01 | 8.1667 | 79.5167 | The FLM team serviced one A/C and confirmed it is working properly. The other A/C remains off, and its compressor replacement is scheduled. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan / Eric
226 | Sirti-WAN-R3-Ticket-201 | NA | 2026-04-27 | P059C1-ENC23-UPE-02 P059C1-ENC23-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB at FP side tripped |  | Zone 71 | 25.4516333° 51.4090805° | Outside Doha | P2 - High | 2026-04-27 14:07 | 2026-04-27 14:11 | 3.3167 | 2026-04-27 14:09 | 2026-04-27 14:22 | 13 | 14.5167 | Main CB at FP was tripped. Devices restored after turning CB ON | Completed | Maintainer | N/a | N/a | Devices Back Online | Rizwan
227 | Sirti-WAN-R3-Ticket-202 | NA | 2026-04-27 | P059C1-ENC04-UPE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC CB was tripped |  | Zone 71 | 25.3653937° 51.4467471° | Outside Doha | P3 - Medium | 2026-04-27 14:19 | 2026-04-27 14:25 | 5.7167 | 2026-04-27 14:45 | 2026-04-27 14:55 | 9.4167 | 35.3167 | The FLM team performed general servicing for the A/C and ensured that the A/C system is working properly | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan / Eric
228 | Sirti-WAN-R3-Ticket-203 | NA | 2026-04-28 | IE5000-6009 | Aaqib | Link Down | WAN Link Down | Optical Rx power for the uplink was very low at P003-ENC41 |  | Zone 61 | 25.3233945337° 51.5360444444° | Outside Doha | P3 - Medium | 2026-04-28 08:22 | 2026-04-28 08:25 | 2.55 | 2026-04-28 09:02 | 2026-04-28 22:18 | 796 | 836 | The FLM team inspected the uplink fiber route, cleaned it, and adjusted the bends at P003-ENC41, which improved the optical power levels and brought the port up. An OTDR test activity has been scheduled to further optimize the optical power. | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Irshad
229 | Sirti-WAN-R3-Ticket-204 | NA | 2026-04-28 | P008C3-ENC25-UPE-02 | Aaqib | CPU Temperature too high | High Temperature | Current temperature is 56°C at SFU board 6 |  | Zone 56 | 51.50261, 25.2341068 | Outside Doha | P3 - Medium | 2026-04-28 13:37 | 2026-04-28 13:42 | 5.0333 | 2026-04-28 15:00 | 2026-04-28 15:23 | 22.9667 | 106 | There is issue with AC and schema maintained by Salam Tech | Completed | Non-maintainer | 3rd Party | Salam Tech | Alarm Cleared | -
230 | Sirti-WAN-R3-Ticket-205 | NA | 2026-04-28 | P003_DWDM | Sanket | Power Modules stopped working | Power module powered off | Power interruption (CB tripped) in control room |  | Zone 66 | 25.3730597 51.5247872 | Outside Doha | P3 - Medium | 2026-04-28 15:13 | 2026-04-28 15:26 | 13 | 2026-04-28 15:26 | 2026-04-28 15:40 | 13.4333 | 26.4333 | As per discussion with Mr.Tahir (EGIS-Control room), The CB is tripped near the fire alarm. No service impact as device working on redundant power modules | Completed | Non-maintainer | 3rd Party | Egis | Alarm Cleared | -
231 | Sirti-WAN-R3-Ticket-206 | NA | 2026-04-28 | P029C2-ENC05-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | MCB tripped at ITS FP |  | Zone 38 | 25.281278° 51.503972° | Inside Doha | P2 - High | 2026-04-28 16:57 | 2026-04-28 17:03 | 5.9167 | 2026-04-28 17:39 | 2026-04-28 18:03 | 23.85 | 65.7667 | The MCB had tripped at the ITS FP. The field engineer turned it back ON, and the device is now reachable. | Completed | Maintainer | N/a | N/a | Devices Back Online | Masthanbasha
232 | Sirti-WAN-R3-Ticket-207 | NA | 2026-04-29 | IE5000-1003 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-04-29 11:20 | 2026-04-29 11:25 | 4.7333 | 2026-04-29 11:25 | 2026-04-29 11:36 | 11.6167 | 16.35 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
233 | Sirti-WAN-R3-Ticket-208 | NA | 2026-04-30 | SAL-ENC67-CE-01 | Abubaker | Link Down | LAN Link Down | Port Auto restored before FLM reach the site |  | Zone 96 | 24.7761642° 50.8665552° | Outside Doha | P3 - Medium | 2026-04-30 04:07 | 2026-04-30 04:18 | 11.2667 | 2026-04-30 04:18 | 2026-04-30 04:31 | 13.4333 | 24.7 | Port GE1/0/9 Auto restored before FLM reach to the site | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | -
234 | Sirti-WAN-R3-Ticket-209 | NA | 2026-05-01 | SAL-ENC20-CE-01 | Abubaker | Link Down | LAN Link Down | Port Auto restored before FLM reach the site |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-05-01 04:34 | 2026-05-01 04:44 | 9.55 | 2026-05-01 04:44 | 2026-05-01 05:00 | 15.5667 | 25.1167 | Port GE1/0/9 Auto restored before FLM reach to the site | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | -
235 | Sirti-WAN-R3-Ticket-210 | NA | 2026-05-01 | SAL-ENC26-CE-01 | Aaqib | Link Down | LAN Link Down | KAHRAMAA power interruption |  | Zone 81 | 25.1435454° 51.2478413° | Outside Doha | P3 - Medium | 2026-05-01 07:36 | 2026-05-01 07:42 | 5.7667 | 2026-05-01 07:42 | 2026-05-01 07:45 | 3.0333 | 8.8 | SAL-ENC26-CE-01 Port 25GE 1/0/4 connected to (S-Node-25) was down due to Kahramaa planned shutdown | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
236 | Sirti-WAN-R3-Ticket-211 | NA | 2026-05-01 | P011-Enc01-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 91 | 25.1812793° 51.5013254° | Outside Doha | P2 - High | 2026-05-01 14:25 | 2026-05-01 14:28 | 3.5667 | 2026-05-01 14:28 | 2026-05-01 14:34 | 5.4833 | 9.05 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
237 | Sirti-WAN-R3-Ticket-212 | NA | 2026-05-01 | P006-ECN17-UPE-02 P006-ENC17-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | There was no power inside the cabinet due to high temperature at cabinet |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-01 16:14 | 2026-05-01 16:17 | 3.3667 | 2026-05-01 16:47 | 2026-05-01 17:03 | 16.3333 | 49.7 | FLM team kept the cabinet open to cool down and scheduled for A/C system inspection | Completed | Non-maintainer | Defect | AC | Devices Back Online | Salem Haj
238 | Sirti-WAN-R3-Ticket-213 | NA | 2026-05-02 | IE5000-1003 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 60 | 25.30462 51.51743 | Outside Doha | P2 - High | 2026-05-02 10:18 | 2026-05-02 10:22 | 4.4 | 2026-05-02 10:22 | 2026-05-02 10:24 | 1.6167 | 6.0167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
239 | Sirti-WAN-R3-Ticket-214 | NA | 2026-05-02 | P006-ECN17-UPE-02 P006-ENC17-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | There was no output power from the UPS due to high temperature inside the cabinet |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-02 15:13 | 2026-05-02 15:16 | 2.8333 | 2026-05-02 15:45 | 2026-05-02 15:58 | 13.2833 | 45.1167 | FLM team restarted the UPS | Completed | Non-maintainer | Defect | AC | Devices Back Online | Hassan
240 | Sirti-WAN-R3-Ticket-215 | NA | 2026-05-02 | P006-ECN17-UPE-02 P006-ENC17-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | A/C system was not working properly, FLM team was on site to repair the A/C system |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-02 19:57 | 2026-05-02 19:59 | 2.3167 | 2026-05-02 20:09 | 2026-05-02 21:27 | 77.6333 | 89.95 | Team replaced faulty Airconditioner condenser fan | Completed | Non-maintainer | Defect | AC | Devices Back Online | Eric
241 | Sirti-WAN-R3-Ticket-216 | NA | 2026-05-03 | P023C1-ENC01-UPE-01 | Aaqib | CPU Temperature too high | High Temperature | Threshold temperature was set high |  | Zone 90 | 25.111748° 51.583897° | Outside Doha | P3 - Medium | 2026-05-03 09:04 | 2026-05-03 09:09 | 5 | 2026-05-03 09:47 | 2026-05-03 09:50 | 2.7833 | 45.9167 | The required temperature in the Cabinet has been set as per the standard level | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Ghulam
242 | Sirti-WAN-R3-Ticket-217 | NA | 2026-05-03 | P028C2-ENC-01-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | MCB was tripped inside WAN Cabinet |  | Zone 7 | 25.283910° 51.5496128° | Inside Doha | P2 - High | 2026-05-03 09:47 | 2026-05-03 09:55 | 7.1833 | 2026-05-03 10:18 | 2026-05-03 10:21 | 3.1167 | 33.5 | Device restored after turning on MCB inside cabinet | Completed | Maintainer | N/a | N/a | Devices Back Online | Irshad
243 | Sirti-WAN-R3-Ticket-218 | NA | 2026-05-03 | P060-ENC179-UPE-02 | Aaqib | CPU Temperature too high | High Temperature | Gas leakage in the AC pipe and Compressor faulty |  | Zone 70 | 25.639484° 51.491537° | Outside Doha | P3 - Medium | 2026-05-03 10:20 | 2026-05-03 10:24 | 3.8 | 2026-05-03 11:28 | 2026-05-03 11:36 | 7.7667 | 75.65 | Detected and repaired refrigerant leakage in the capillary tube, replaced the filter drier, performed system vacuuming, refilled R134a refrigerant, and completed general servicing of the unit. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Ghulam
244 | Sirti-WAN-R3-Ticket-219 | NA | 2026-05-03 | P011-Enc26-CE-01 | Aaqib | CPU Temperature too high | High Temperature | AC Compressor faulty |  | Zone 50 | 25.22234, 51.542 | Outside Doha | P3 - Medium | 2026-05-03 10:53 | 2026-05-03 10:58 | 5.1833 | 2026-05-03 12:41 | 2026-05-03 12:57 | 15.35 | 123.4667 | The compressor, fan, and 40+5 capacitor were replaced | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
245 | Sirti-WAN-R3-Ticket-220 | NA | 2026-05-03 | P023C3-ENC174-UPE-02 | Aaqib | CPU Temperature too high | High Temperature | Threshold temperature was set high |  | Zone 94 | 25.01688 , 51.49047 | Outside Doha | P3 - Medium | 2026-05-03 12:17 | 2026-05-03 12:22 | 5.1333 | 2026-05-03 14:15 | 2026-05-03 14:18 | 2.75 | 120.7333 | Cabinet temperature normalized after setting temperatures parameters in AC controller | Completed | Non-maintainer | Defect | AC | Devices Back Online | Ghulam
246 | Sirti-WAN-R3-Ticket-221 | NA | 2026-05-03 | P008C3-Enc01-UPE-01 | Aaqib | CPU Temperature too high | High Temperature | Schema Under Salam technology |  | Zone 55 | 25.2614822° 51.4801647° | Outside Doha | P3 - Medium | 2026-05-03 13:45 | 2026-05-03 13:51 | 6.25 | 2026-05-03 14:07 | 2026-05-03 14:17 | 10.2 | 32.2833 | Schema Under Salam tech. Escalated to Mr.Salman | Completed | Non-maintainer | 3rd Part (Salam Tech) | N/a | Alarm Cleared | -
247 | Sirti-WAN-R3-Ticket-222 | NA | 2026-05-03 | P010-Enc01-CE-01 | Aaqib | CPU Temperature too high | High Temperature | Threshold temperature was set high |  | Zone 81 | 25.139881, 51.407393 | Outside Doha | P3 - Medium | 2026-05-03 14:16 | 2026-05-03 14:19 | 2.65 | 2026-05-03 14:35 | 2026-05-03 14:46 | 11.1667 | 29.95 | The required temperature in the Cabinet has been set as per the standard level | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Ghulam
248 | Sirti-WAN-R3-Ticket-223 | NA | 2026-05-03 | SAL-ENC09-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-05-03 20:33 | 2026-05-03 20:35 | 1.65 | 2026-05-03 20:33 | 2026-05-03 20:35 | 1.9833 | 1.9833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
249 | Sirti-WAN-R3-Ticket-224 | NA | 2026-05-04 | IE5000-1003 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 60 | 25.30462° 51.51743° | Outside Doha | P2 - High | 2026-05-04 12:27 | 2026-05-04 12:32 | 5 | 2026-05-04 12:32 | 2026-05-04 12:50 | 17 | 22 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
250 | Sirti-WAN-R3-Ticket-225 | NA | 2026-05-04 | IE5000-1702 | Aaqib | Optical module Temperature too High | High Temperature | No AC installed in cabinet and Exhaust Fan not working |  | Zone 18 | 25.2833249904° 51.551376977° | Inside Doha | P3 - Medium | 2026-05-04 13:27 | 2026-05-04 13:29 | 2.6 | 2026-05-04 13:57 | 2026-05-04 14:03 | 6.1667 | 36.15 | FLM replaced faulty exhaust FAN | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Irshad/
251 | Sirti-WAN-R3-Ticket-226 | NA | 2026-05-04 | 22FEB-ENC01-CE-01 | Aaqib | Optical module Temperature too High | High Temperature | Threshold temperature was set high |  | Zone 43 | 25.2453756° 51.5148756° | Outside Doha | P3 - Medium | 2026-05-04 14:40 | 2026-05-04 14:42 | 1.75 | 2026-05-04 16:40 | 2026-05-04 16:47 | 6.4667 | 126.4667 | alarm is auto cleared before reaching the site , FLM visited and set the temperature thermostat of the AC from 32C to 28C | Completed | Non-maintainer | Defect | N/a | Alarm Cleared | Khadar
252 | Sirti-WAN-R3-Ticket-227 | NA | 2026-05-05 | P003-ENC40-UPE-02 | Sanket | Power Modules stopped working | Power module powered off | KAHRAMAA power interruption |  | Zone 65 | 25.3344995° 51.5180512° | Outside Doha | P3 - Medium | 2026-05-05 04:50 | 2026-05-05 04:51 | 1 | 2026-05-05 04:51 | 2026-05-05 04:52 | 1.3 | 2.3 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
253 | Sirti-WAN-R3-Ticket-228 | NA | 2026-05-05 | RAA-ENC01-CE-01 | Aaqib | Link down | LAN Link Down | Auto Restored |  | Zone 27 | 25.284123° 51.5558539° | Inside Doha | P3 - Medium | 2026-05-05 11:28 | 2026-05-05 11:35 | 7.3833 | 2026-05-05 11:35 | 2026-05-05 12:01 | 25.7333 | 33.1167 | Alarm Auto Restored | Completed | Non-maintainer | N/a | N/a | Alarm Cleared | Hichem
254 | Sirti-WAN-R3-Ticket-229 | NA | 2026-05-05 | P023C3-ENC174-UPE-02 | Aaqib | CPU Temperature too high | High Temperature | AC working but not cooling |  | Zone 94 | 25.01688 , 51.49047 | Outside Doha | P3 - Medium | 2026-05-05 12:03 | 2026-05-05 12:13 | 9.95 | 2026-05-05 13:01 | 2026-05-05 13:21 | 20.4667 | 78.6167 | The compressor cable had been disconnected; we simply reconnected it | Completed | Non-maintainer | Defect | N/a | Alarm Cleared | Eric
255 | Sirti-WAN-R3-Ticket-230 | NA | 2026-05-05 | P007C1-ENC31-UPE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 52 | 25.306727 51.411587 | Outside Doha | P2 - High | 2026-05-05 12:59 | 2026-05-05 13:09 | 10.55 | 2026-05-05 13:09 | 2026-05-05 13:36 | 27.0833 | 37.6333 | Kahramaa planned shutdown | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
256 | Sirti-WAN-R3-Ticket-231 | NA | 2026-05-05 | P009C3-ENC01-CE-01 | Aaqib | Optical module Temperature too High | High Temperature | AC working but not cooling |  | Zone 56 | 25.22135257° 51.4353355° | Outside Doha | P3 - Medium | 2026-05-05 13:36 | 2026-05-05 13:43 | 6.85 | 2026-05-05 13:55 | 2026-05-05 16:27 | 151.55 | 170.55 | Alarm Auto restored before FLM reached the site however when FLM team reached the site they did overall inspection for the A/C system and rectified & adjusted the air conditioning settings and thermostat to ensure improved cooling performance. | Completed | Non-maintainer | Defect | N/a | Alarm Cleared | Khadar
257 | Sirti-WAN-R3-Ticket-232 | NA | 2026-05-05 | SAL-ENC32-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 82 | 25.1165799° 51.1812367° | Outside Doha | P2 - High | 2026-05-05 15:47 | 2026-05-05 15:51 | 3.8333 | 2026-05-05 15:51 | 2026-05-05 15:53 | 1.7167 | 5.55 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
258 | Sirti-WAN-R3-Ticket-233 | NA | 2026-05-05 | P023C3-ENC174-UPE-02 P023C3-ENC174-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 94 | 25.01688 , 51.49047 | Outside Doha | P2 - High | 2026-05-05 18:49 | 2026-05-05 18:53 | 4 | 2026-05-05 18:53 | 2026-05-05 19:01 | 8.0667 | 12.0667 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
259 | Sirti-WAN-R3-Ticket-234 | NA | 2026-05-06 | P004-ENC43-CE-01 P004-ENC43-UPE-02 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | FLM Found RCCB tripped at ITS cabiet |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P2 - High | 2026-05-06 07:29 | 2026-05-06 07:34 | 5 | 2026-05-06 07:40 | 2026-05-06 08:14 | 33.5667 | 44.5667 | FLM switched on tripped CB at cabinet side | Completed | Maintainer | N/a | N/a | Alarm Cleared | Hichem
260 | Sirti-WAN-R3-Ticket-235 | NA | 2026-05-06 | P023C2-ENC43-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P2 - High | 2026-05-06 07:29 | 2026-05-06 07:35 | 5.75 | 2026-05-06 07:35 | 2026-05-06 08:13 | 37.7667 | 43.5167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Irshad
261 | Sirti-WAN-R3-Ticket-236 | NA | 2026-05-06 | SAL-ENC20-CE-01 | AMR | Power Modules stopped working | Power Modules stopped working | FLM Checked the power at the cabinet and found that the UPS has no output. |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-05-06 12:30 | 2026-05-06 12:35 | 5 | 2026-05-06 12:42 | 2026-05-06 13:35 | 53.15 | 65.15 | FLM performed a restart of the UPS. | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hichem
262 | Sirti-WAN-R3-Ticket-237 | NA | 2026-05-06 | SAL-ENC26-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 81 | 25.1435454° 51.2478413° | Outside Doha | P2 - High | 2026-05-06 12:32 | 2026-05-06 12:37 | 5 | 2026-05-06 12:37 | 2026-05-06 13:34 | 57.3333 | 62.3333 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Najeeb
263 | Sirti-WAN-R3-Ticket-238 | NA | 2026-05-07 | P006-ENC17-UPE-02 P006-ENC17-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for UPS replacement |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-07 02:32 | 2026-05-07 02:33 | 1 | 2026-05-07 02:36 | 2026-05-07 02:48 | 11.6 | 15.1667 | Planned activity for UPS replacement | Completed | Non-maintainer | 3rd Party | N/a | Devices Back Online | Ghulam
264 | Sirti-WAN-R3-Ticket-239 | NA | 2026-05-07 | P006-ENC17-UPE-02 P006-ENC17-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for UPS replacement |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-07 03:15 | 2026-05-07 03:18 | 3 | 2026-05-07 03:19 | 2026-05-07 03:29 | 10.0833 | 14.0833 | Planned activity for UPS replacement | Completed | Non-maintainer | 3rd Party | N/a | Devices Back Online | Ghulam
265 | Sirti-WAN-R3-Ticket-240 | NA | 2026-05-07 | P006-ENC17-UPE-02 P006-ENC17-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for UPS replacement |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-07 03:41 | 2026-05-07 03:43 | 2 | 2026-05-07 03:44 | 2026-05-07 03:55 | 10.2667 | 13.2667 | Planned activity for UPS replacement | Completed | Non-maintainer | 3rd Party | N/a | Devices Back Online | Ghulam
266 | Sirti-WAN-R3-Ticket-241 | NA | 2026-05-07 | SAL-ENC09-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-05-07 09:32 | 2026-05-07 09:33 | 1 | 2026-05-07 09:33 | 2026-05-07 09:35 | 2 | 3 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
267 | Sirti-WAN-R3-Ticket-242 | NA | 2026-05-07 | P008C3-ENC25-UPE-02 | Adel | CPU Temperature too high | High Temperature | Current temperature is 58°C at SFU board 6 |  | Zone 56 | 51.50261, 25.2341068 | Outside Doha | P3 - Medium | 2026-05-07 13:11 | 2026-05-07 13:13 | 2 | 2026-05-07 13:26 | 2026-05-07 14:38 | 72 | 87 | There is issue with AC and schema maintained by Salam Tech | Completed | Non-maintainer | 3rd Party | Salam Tech | Alarm Cleared | -
268 | Sirti-WAN-R3-Ticket-243 | NA | 2026-05-07 | P007C1-ENC31-UPE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no Karomaa power at cabinet side |  | Zone 52 | 25.306727 51.411587 | Outside Doha | P2 - High | 2026-05-07 13:23 | 2026-05-07 13:25 | 2.1167 | 2026-05-07 14:35 | 2026-05-07 14:57 | 21.9 | 94.0167 | CB tripped at FP side due to a short circuit on A/C. Site restored after turning on CB | Completed | Non-maintainer | Defect | N/a | Devices Back Online | hicham
269 | Sirti-WAN-R3-Ticket-244 | NA | 2026-05-07 | 22FEB-ENC25-CE-01 | Adel | Optical module temperature too high | High Temperature | High Temperature inside the Cabinet |  | Zone 51 | 25.31832397, 51.47088144 | Outside Doha | P3 - Medium | 2026-05-07 13:44 | 2026-05-07 13:46 | 2 | 2026-05-07 13:46 | 2026-05-07 14:54 | 67.8167 | 69.8167 | The compressor was not working. Then adjusted the AC function settings and temperature on the thermostat control system. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Sanjeewa
270 | Sirti-WAN-R3-Ticket-245 | NA | 2026-05-07 | SAL-ENC09-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-05-07 13:50 | 2026-05-07 13:52 | 2 | 2026-05-07 13:52 | 2026-05-07 13:53 | 1 | 3 | Cheked the power cables & the voltage at the MCB, found a loose connection for the power cable at the terminal blocks | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Khadar
271 | Sirti-WAN-R3-Ticket-246 | NA | 2026-05-07 | SAL-ENC09-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for fixing the power cables properly to the terminal blocks |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-05-07 15:11 | 2026-05-07 15:18 | 7 | 2026-05-07 15:26 | 2026-05-07 15:41 | 15 | 30 | Disconnected the power cables from terminal blocks, replaced the cable lugs and reconnected and tightened the cables to the power terminal blocks | Completed | Non-maintainer | Planned Activity | N/a | Devices Back Online | Khadar
272 | Sirti-WAN-R3-Ticket-247 | NA | 2026-05-07 | 22FEB-ENC25-CE-01 | Abubaker | Link down | Link Down | Found high Temp at the cabinet as A/C is not cooling properly |  | Zone 51 | 25.31832397, 51.47088144 | Outside Doha | P3 - Medium | 2026-05-07 15:45 | 2026-05-07 15:56 | 11 | 2026-05-07 15:56 | 2026-05-07 16:08 | 12 | 23 | Port went down during FLM troubleshooting the high Temp issue on site | Completed | Non-maintainer | Defect | N/a | Devices Back Online | Sanjeewa
273 | Sirti-WAN-R3-Ticket-248 | NA | 2026-05-08 | SAL-ENC20-CE-01 | Sanket | Power Modules stopped working | Power Modules stopped working | The UPS has no output. |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-05-08 03:40 | 2026-05-08 03:43 | 3.1667 | 2026-05-08 04:20 | 2026-05-08 05:09 | 49.1667 | 89.3333 | FLM performed a restart of the UPS. | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Umair
274 | Sirti-WAN-R3-Ticket-249 | NA | 2026-05-08 | SAL-ENC20-CE-01 | Sanket | Link down | LAN Link Down | While Trouble shooting of UPS issue, the link was down (GE 1/0/9) |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-05-08 04:31 | 2026-05-08 04:32 | 1.0167 | 2026-05-08 04:32 | 2026-05-08 04:33 | 0.46667 | 1.4833 | While Trouble shooting of UPS issue, The link is down towards LAN | Completed | Non-maintainer | 3rd Party | RMC | Alarm Cleared | Umair
275 | Sirti-WAN-R3-Ticket-250 | NA | 2026-05-08 | SAL-ENC45-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The power socket live cable has shorted, which caused the socket breaker to trip. The breaker tripped due to this fault |  | Zone 83 | 25.005944° 51.042739° | Outside Doha | P2 - High | 2026-05-08 04:42 | 2026-05-08 04:47 | 5.0833 | 2026-05-08 06:00 | 2026-05-08 06:09 | 8.7167 | 86.8333 | Removed the shorted cable from the power socket, fixed the wiring properly, and reset the breaker. | Completed | Maintainer | N/a | N/a | Devices Back Online | Umair
276 | Sirti-WAN-R3-Ticket-251 | NA | 2026-05-08 | DUK-DBR-UPE-01 DUK-DBR-USG-01 DUK-DBR-USG-02 | Sanket | Power Modules stopped working | Power Modules stopped working | UPS DB-03 Main breaker was tripped |  | Zone 80 | 25.3775425 51.22843816 | Outside Doha | P3 - Medium | 2026-05-08 06:37 | 2026-05-08 06:43 | 6 | 2026-05-08 07:28 | 2026-05-08 07:59 | 30.6 | 82.0667 | FLM switched on tripped main CB at UPS DB-03 | Completed | Non-maintainer | Defect | UPS | Devices Back Online | nageeb
277 | Sirti-WAN-R3-Ticket-252 | NA | 2026-05-08 | P004-MOQ-CE-01 | Adel | Link down | LAN Link Down | UPS DB-03 Main breaker was tripped |  | Zone 51 | 25.319385 51.352255 | Outside Doha | P3 - Medium | 2026-05-08 06:37 | 2026-05-08 06:40 | 3 | 2026-05-08 07:35 | 2026-05-08 08:04 | 28.6833 | 87.1667 | FLM switched on tripped main CB at UPS DB-03 | Completed | Non-maintainer | Defect | UPS | Devices Back Online | irshad
278 | Sirti-WAN-R3-Ticket-253 | NA | 2026-05-08 | CRR-ENC14-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 41 | 25.26272 51.52569 | Inside Doha | P2 - High | 2026-05-08 21:05 | 2026-05-08 21:09 | 3.6667 | 2026-05-08 21:05 | 2026-05-08 21:27 | 21.7667 | 21.7667 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
279 | Sirti-WAN-R3-Ticket-254 | NA | 2026-05-08 | CRR-ENC14-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 41 | 25.26272 51.52569 | Inside Doha | P2 - High | 2026-05-08 21:40 | 2026-05-08 21:40 | 0.33333 | 2026-05-08 21:40 | 2026-05-08 22:01 | 21.7833 | 21.7833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
280 | Sirti-WAN-R3-Ticket-255 | NA | 2026-05-10 | P007C2-ENC99-UPE-02 | Adel | CPU Temperature too high | High Temperature | AC CB was tripped and AC is not working |  | Zone 54 | 25.2967109° 51.4488814° | Outside Doha | P3 - Medium | 2026-05-10 11:24 | 2026-05-10 11:26 | 2 | 2026-05-10 12:06 | 2026-05-10 14:17 | 130.6833 | 172.3333 | AC is now functioning properly after the following work was completed: installation of a new 250mm compressor fan, replacement of the PCB controller, repair of the single-phase dual motor evaporator fan, and fitting of both an 8 µF capacitor and a 35 µF capacitor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
281 | Sirti-WAN-R3-Ticket-256 | NA | 2026-05-10 | P007C1-ENC31-UPE-01 | Adel | Temperature higher than Upper threshold | High Temperature | High Temperature inside the Cabinet |  | Zone 52 | 25.306727 51.411587 | Outside Doha | P3 - Medium | 2026-05-10 13:15 | 2026-05-10 13:17 | 2 | 2026-05-10 13:30 | 2026-05-10 13:36 | 6.0833 | 20.7333 | AC1 is cooling well, and AC2 was serviced with a new SECOP SC15G compressor, capacitor, refrigerant refill, and thorough cleaning; after testing, both units are now working and cooling efficiently. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
282 | Sirti-WAN-R3-Ticket-257 | NA | 2026-05-10 | P005-ENC414-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 51 | 25.3335964° 51.4482522° | Outside Doha | P2 - High | 2026-05-10 15:08 | 2026-05-10 15:11 | 3 | 2026-05-10 15:12 | 2026-05-10 15:13 | 1.75 | 5.75 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
283 | Sirti-WAN-R3-Ticket-258 | NA | 2026-05-10 | P007C2-ENC99-UPE-02 | Sanket | CPU Temperature too high | High Temperature | The capacitor (40Plus5) is faulty, and the fan unit is also faulty. |  | Zone 54 | 25.2967109° 51.4488814° | Outside Doha | P3 - Medium | 2026-05-10 15:32 | 2026-05-10 15:40 | 7.8167 | 2026-05-10 16:25 | 2026-05-10 16:31 | 5.6833 | 58.5 | AC is now operating smoothly after the following work was carried out: installation of a new 250mm compressor fan, replacement of the PCB controller, repair of the single-phase dual motor evaporator fan, and the addition of both an 8 µF capacitor and a 35 µF capacitor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
284 | Sirti-WAN-R3-Ticket-259 | NA | 2026-05-11 | P023C1-ENC01-UPE-01 | Adel | Temperature higher than Upper threshold | High Temperature | Required: Nitrogen gas, vacuum cleaning, and R134a gas refill. |  | Zone 90 | 25.111748° 51.583897° | Outside Doha | P3 - Medium | 2026-05-11 13:04 | 2026-05-11 13:06 | 2 | 2026-05-11 14:34 | 2026-05-11 14:38 | 4.1667 | 93.8667 | Attended site for AC cooling issue, carried out full inspection, replaced faulty compressor and related components, cleaned and flushed the system, recharged refrigerant, and tested successfully—unit now cooling properly, though sensor cable replacement is still pending and will be completed today. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
285 | Sirti-WAN-R3-Ticket-260 | NA | 2026-05-11 | P007C2-ENC99-UPE-02 | Sanket | CPU Temperature too high | High Temperature | The capacitor (40Plus5) is faulty, and the fan unit is also faulty. |  | Zone 54 | 25.2967109° 51.4488814° | Outside Doha | P3 - Medium | 2026-05-11 14:32 | 2026-05-11 14:42 | 9.6333 | 2026-05-11 15:25 | 2026-05-11 15:43 | 18.3667 | 71 | AC is now functioning as expected following the installation of a new 250mm compressor fan, replacement of the PCB controller, repair of the single-phase dual motor evaporator fan, and the addition of both an 8 µF capacitor and a 35 µF capacitor. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
286 | Sirti-WAN-R3-Ticket-261 | NA | 2026-05-11 | CRR-ENC16-UPE-01 | Sanket | CPU Temperature too high | High Temperature | High Temperature inside the Cabinet |  | Zone 42 | 25.2590324° 51.537498° | Inside Doha | P3 - Medium | 2026-05-11 15:49 | 2026-05-11 15:54 | 4.6 | 2026-05-11 15:55 | 2026-05-11 16:00 | 5.7333 | 11.3333 | Alarm Auto restored before FLM reached the site | Completed | Non-maintainer | Defect | AC | Alarm Cleared | -
287 | Sirti-WAN-R3-Ticket-262 | NA | 2026-05-11 | P010-ENC61-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-05-11 20:38 | 2026-05-11 20:42 | 4 | 2026-05-11 20:45 | 2026-05-11 20:47 | 1.2667 | 8.2667 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
288 | Sirti-WAN-R3-Ticket-263 | NA | 2026-05-11 | P010-ENC61-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-05-11 21:39 | 2026-05-11 21:41 | 2 | 2026-05-11 21:41 | 2026-05-11 21:44 | 3.2667 | 5.2667 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
289 | Sirti-WAN-R3-Ticket-264 | NA | 2026-05-11 | P012-ENC30-USG-01 P012_Pri | Sanket | Power Modules stopped working | Power Modules stopped working | CB was found tripped. 1 power module in DWDM is faulty |  | Zone 56 | 25.2162349° 51.5021362° | Outside Doha | P3 - Medium | 2026-05-11 21:41 | 2026-05-11 21:49 | 7.15 | 2026-05-11 23:43 | 2026-05-12 | 17 | 138.55 | During the team’s visit, it was found that the AC breaker had tripped. After switching it back on, all modules were restored except one power module in the DWDM system. The FLM team confirmed that the power cable was receiving power, but when the module was swapped with another chassis, it still failed to operate. Based on these findings, the issue is suspected to be a faulty AC board that caused the breaker to trip. Not Sirti AC and Sirti team attended and made safe and left. Fault to be closed from Sirti side. | Completed | Non-maintainer | 3rd Party | Others | Devices Not affected | Umar and Hassan
290 | Sirti-WAN-R3-Ticket-265 | NA | 2026-05-11 | P010-ENC61-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | 1 Power Supply found faulty |  | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-05-11 23:39 | 2026-05-11 23:41 | 2.5833 | 2026-05-11 23:41 | 2026-05-11 23:50 | 8.5167 | 11.1 | Power supply replacement Done | Completed | Maintainer | N/a | N/a | Devices Back Online | Sarjoon
291 | Sirti-WAN-R3-Ticket-266 | NA | 2026-05-12 | P010-ENC61-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device went down during replacement of Power supply |  | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-05-12 00:26 | 2026-05-12 00:28 | 2.2333 | 2026-05-12 00:28 | 2026-05-12 00:32 | 3.7 | 5.9333 | Power cables arrangement during the activity | Completed | Non-maintainer | Planned Activity | N/a | Devices Back Online | Sarjoon
292 | Sirti-WAN-R3-Ticket-267 | NA | 2026-05-12 | P014-Enc13-UPE-02 P014-Enc13-DSW13 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 45 | 25.257307° 51.549776° | Outside Doha | P2 - High | 2026-05-12 03:44 | 2026-05-12 03:45 | 1.65 | 2026-05-12 03:45 | 2026-05-12 03:48 | 3.1 | 4.75 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
293 | Sirti-WAN-R3-Ticket-268 | NA | 2026-05-12 | P014-Enc13-UPE-02 P014-Enc13-DSW13 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 45 | 25.257307° 51.549776° | Outside Doha | P2 - High | 2026-05-12 04:19 | 2026-05-12 04:22 | 3.25 | 2026-05-12 04:22 | 2026-05-12 04:24 | 1.5667 | 4.8167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
294 | Sirti-WAN-R3-Ticket-269 | NA | 2026-05-12 | SAL-ENC32-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 82 | 25.1165799° 51.1812367° | Outside Doha | P2 - High | 2026-05-12 07:38 | 2026-05-12 07:40 | 2.15 | 2026-05-12 08:28 | 2026-05-12 10:02 | 93.7167 | 143.8667 | Kahramaa planned shutdown., FLM installed temporary PG to restore devices | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Najeeb
295 | Sirti-WAN-R3-Ticket-270 | NA | 2026-05-12 | SAL-ENC32-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 82 | 25.1165799° 51.1812367° | Outside Doha | P2 - High | 2026-05-12 12:13 | 2026-05-12 12:14 | 1 | 2026-05-12 12:14 | 2026-05-12 12:19 | 4.6667 | 5.6667 | FLM disconnected PG and Kahramma power is restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Najeeb
296 | Sirti-WAN-R3-Ticket-271 | NA | 2026-05-12 | CRR-ENC16-UPE-01 | Adel | CPU Temperature too high | High Temperature | AC is not cooling |  | Zone 42 | 25.2590324° 51.537498° | Inside Doha | P3 - Medium | 2026-05-12 12:10 | 2026-05-12 12:14 | 4 | 2026-05-12 13:30 | 2026-05-12 13:33 | 2.8333 | 82.8333 | AC unit was inspected and power checked, with the leak repaired, gas refilled, and thorough cleaning performed; as a result, the AC is now cooling properly and operating in good condition | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Najeeb
297 | Sirti-WAN-R3-Ticket-272 | NA | 2026-05-12 | P010-ENC89-UPE-02 | Adel | CPU Temperature too high | High Temperature | AC is not cooling |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | P3 - Medium | 2026-05-12 14:01 | 2026-05-12 14:03 | 2 | 2026-05-12 14:08 | 2026-05-12 14:10 | 1.6667 | 8.6667 | Reset the AC function settings and temperature in the thermostat. Cleaned the AC control system with an air blower. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
298 | Sirti-WAN-R3-Ticket-273 | NA | 2026-05-12 | P007C2-ENC99-UPE-02 P007C2-ENC99-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The FLM team is troubleshooting the AC issue |  | Zone 54 | 25.2967109° 51.4488814° | Outside Doha | P2 - High | 2026-05-12 15:09 | 2026-05-12 15:12 | 3 | 2026-05-12 15:12 | 2026-05-12 15:23 | 11.2833 | 14.2833 | During AC troubleshooting, the MCB was tripped OFF. After switching it ON, the device is now reachable | Completed | Non-maintainer | Defect | AC | Devices Back Online | Rizwan
299 | Sirti-WAN-R3-Ticket-274 | NA | 2026-05-12 | CRR-ENC16-UPE-01 CRR-ENC16-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The FLM team is troubleshooting the AC issue |  | Zone 42 | 25.2590324° 51.537498° | Inside Doha | P2 - High | 2026-05-12 18:49 | 2026-05-12 18:50 | 1 | 2026-05-12 18:51 | 2026-05-12 18:55 | 3.9167 | 5.9167 | During AC troubleshooting, the MCB was tripped OFF. After switching it ON, the device is now reachable | Completed | Non-maintainer | Defect | AC | Devices Back Online | Eric
300 | Sirti-WAN-R3-Ticket-275 | NA | 2026-05-12 | SAL-ENC20-UPE-01 | Sanket | Power Modules stopped working | Power Modules stopped working | Alarm Auto restored before FLM reached the site |  | Zone 82 | 25.1435454° 51.2478413° | Outside Doha | P3 - Medium | 2026-05-12 19:06 | 2026-05-12 19:10 | 3.6167 | 2026-05-12 19:11 | 2026-05-12 19:12 | 1.1167 | 5.7333 | Alarm Auto restored before FLM reached the site | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | -
301 | Sirti-WAN-R3-Ticket-276 | NA | 2026-05-13 | P005-TCR-CE-01 | Aaqib | Link Down | LAN Link Down | Link connected to Access switch at tunnel |  | Zone 51 | 25.3199307 51.447548 | Outside Doha | P3 - Medium | 2026-05-13 01:07 | 2026-05-13 01:15 | 8.1667 | 2026-05-13 01:07 | 2026-05-13 01:44 | 37.3667 | 37.3667 | Link is connected to access Switch installed inside P005 tunnel and auto restored just before FLM reaching site | Completed | Non-maintainer | 3rd Party | N/a | Alarm Cleared | -
302 | Sirti-WAN-R3-Ticket-276 | NA | 2026-05-13 | P005-TCR-CE-02 | Aaqib | Link Down | LAN Link Down | Link connected to Access switch at tunnel |  | Zone 51 | 25.3199307 51.447548 | Outside Doha | P3 - Medium | 2026-05-13 01:07 | 2026-05-13 01:15 | 8.1667 | 2026-05-13 01:07 | 2026-05-13 01:44 | 37.3833 | 37.3833 | Link is connected to access Switch installed inside P005 tunnel and auto restored just before FLM reaching site | Completed | Non-maintainer | 3rd Party | N/a | Alarm Cleared | -
303 | Sirti-WAN-R3-Ticket-277 | NA | 2026-05-13 | P023C3-ENC174-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device CB in PDU was found tripped inside cabinet |  | Zone 94 | 25.01688 , 51.49047 | Outside Doha | P2 - High | 2026-05-13 05:21 | 2026-05-13 05:25 | 4.35 | 2026-05-13 05:52 | 2026-05-13 05:58 | 5.8333 | 37.4167 | Device restored after turning on CB in PDU | Completed | Maintainer | N/a | N/a | Alarm Cleared | Umair
304 | Sirti-WAN-R3-Ticket-278 | NA | 2026-05-13 | 22FEB-ENC13-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 55 | 25.27506948° 51.48993629° | Outside Doha | P2 - High | 2026-05-13 06:18 | 2026-05-13 06:20 | 2.0667 | 2026-05-13 06:20 | 2026-05-13 06:24 | 3.8833 | 5.95 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
305 | Sirti-WAN-R3-Ticket-279 | NA | 2026-05-13 | P023C3-ENC174-UPE-02 P023C3-ENC174-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | AC CB is tripped (short-circuit) and tripping other devices CBs |  | Zone 94 | 25.01688 , 51.49047 | Outside Doha | P2 - High | 2026-05-13 09:08 | 2026-05-13 09:10 | 2 | 2026-05-13 10:03 | 2026-05-13 11:01 | 57.6 | 112.2333 | FLM switched off defected AC to restore the switches | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
306 | Sirti-WAN-R3-Ticket-280 | NA | 2026-05-13 | P007C2-ENC99-UPE-02 | Adel | CPU Temperature too high | High Temperature | Compressor high Amp and overheating, |  | Zone 54 | 25.2967109° 51.4488814° | Outside Doha | P3 - Medium | 2026-05-13 13:17 | 2026-05-13 13:19 | 2 | 2026-05-13 13:51 | 2026-05-13 13:54 | 2.6667 | 36.6667 | At site P007C2-ENC99-UPE-02, the faulty compressor was replaced and the system serviced, but cooling failed as the new compressor overheated and tripped despite other components testing normal; abnormal performance was confirmed under load, so the unit was removed, returned, and a replacement collected, with further work handed over to the next shift. We installed a new AC compressor, checked the fan connections, and refilled the refrigerant gas. After testing, the unit is now operating properly with strong cooling performance | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan
307 | Sirti-WAN-R3-Ticket-281 | NA | 2026-05-13 | P007C5P1-ENC06-UPE-02 | Adel | Temperature higher than Upper threshold | High Temperature | Capacitor and Compressor is faulty |  | Zone 55 | 25.2694167° 51.4767778° | Outside Doha | P3 - Medium | 2026-05-13 13:27 | 2026-05-13 13:29 | 2 | 2026-05-13 14:16 | 2026-05-13 14:18 | 2 | 50.9833 | Leak repaired, gas refilled, compressor replaced, and full cleaning completed and AC is working normally | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
308 | Sirti-WAN-R3-Ticket-282 | NA | 2026-05-13 | P010-ENC89-UPE-02 | Adel | CPU Temperature too high | High Temperature | AC compressor is not functioning |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | P3 - Medium | 2026-05-13 13:34 | 2026-05-13 13:37 | 3 | 2026-05-13 14:42 | 2026-05-13 14:59 | 17.15 | 85.3667 | Check the cabinet AC compressor to confirm it is not functioning. Then verify the AC status, power supply, and voltage. After that, turn off the AC power and restart the system. Once restarted, the physical AC unit operates normally, and all components are running properly. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
309 | Sirti-WAN-R3-Ticket-283 | NA | 2026-05-13 | P010-ENC01-UPE01 | Adel | CPU Temperature too high | High Temperature | AC is not cooling |  | Zone 81 | 25.1398815° 51.4073931° | Outside Doha | P3 - Medium | 2026-05-13 14:30 | 2026-05-13 14:32 | 2 | 2026-05-13 14:45 | 2026-05-13 14:46 | 1 | 16.8333 | Checked cabinet AC compressor — not working. Verified power and voltage. Restarted AC power, adjusted settings and thermostat. Compressor is now running. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
310 | Sirti-WAN-R3-Ticket-284 | NA | 2026-05-13 | DUK-DBR-UPE-01 DUK-DBR-USG-01 DUK-DBR-USG-02 | Sanket | Power Modules stopped working | Power Modules stopped working | UPS DB-03 Main breaker was tripped at DUK-DBR |  | Zone 80 | 25.3775425 51.22843816 | Outside Doha | P3 - Medium | 2026-05-13 19:16 | 2026-05-13 19:19 | 3.2667 | 2026-05-13 20:25 | 2026-05-13 20:42 | 16.25 | 85.5167 | FLM switched on tripped main CB at UPS DB-03 at DUK-DBR | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hassan
311 | Sirti-WAN-R3-Ticket-284 | NA | 2026-05-13 | P004-MOQ-CE-01 DUK-DBR-USG-01 DUK-DBR-USG-02 | Sanket | Link down | LAN Link Down | UPS DB-03 Main breaker was tripped at DUK-DBR |  | Zone 51 | 25.319385 51.352255 | Outside Doha | P3 - Medium | 2026-05-13 19:16 | 2026-05-13 19:20 | 4.1 | 2026-05-13 20:25 | 2026-05-13 20:47 | 21.45 | 90.7667 | FLM switched on tripped main CB at UPS DB-03 at DUK-DBR | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hassan
312 | Sirti-WAN-R3-Ticket-285 | NA | 2026-05-13 | P012-ENC101-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 57 | 25.1957136° 51.4525682° | Outside Doha | P2 - High | 2026-05-13 20:37 | 2026-05-13 20:39 | 2 | 2026-05-13 20:40 | 2026-05-13 20:41 | 1.4167 | 4.0833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
313 | Sirti-WAN-R3-Ticket-286 | NA | 2026-05-13 | P012-ENC101-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | During ASW-ENC99 (LAN) troubleshooting, the MCB was tripped OFF. After switching it ON, the device is now reachable |  | Zone 57 | 25.1957136° 51.4525682° | Outside Doha | P2 - High | 2026-05-13 22:04 | 2026-05-13 22:06 | 2 | 2026-05-13 22:10 | 2026-05-13 22:11 | 1.3333 | 7 | During ASW-ENC99 (LAN) troubleshooting, the MCB was tripped OFF. After switching it ON, the device is now reachable | Completed | Non-maintainer | Planned Activity | N/a | Devices Back Online | Masthanbasha
314 | Sirti-WAN-R3-Ticket-287 | NA | 2026-05-13 | P006-ENC17-UPE-02 P006-ENC17-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-13 22:08 | 2026-05-13 22:11 | 3 | 2026-05-13 22:12 | 2026-05-13 22:13 | 1.0833 | 5.2833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
315 | Sirti-WAN-R3-Ticket-287 | NA | 2026-05-13 | P006-ENC02-UPE-01 P006-ENC02-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-13 22:21 | 2026-05-13 22:24 | 3 | 2026-05-13 22:25 | 2026-05-13 22:26 | 0.78333 | 4.95 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
316 | Sirti-WAN-R3-Ticket-288 | NA | 2026-05-14 | P010-ENC61-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Planned UPS replacement activity |  | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-05-14 01:26 | 2026-05-14 01:28 | 2.4667 | 2026-05-14 01:28 | 2026-05-14 01:34 | 5.65 | 8.1167 | Planned UPS replacement activity | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Ghulam
317 | Sirti-WAN-R3-Ticket-289 | NA | 2026-05-14 | P010-ENC61-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Planned UPS replacement activity |  | Zone 57 | 25.1700975° ,51.4699752° | Outside Doha | P2 - High | 2026-05-14 04:57 | 2026-05-14 05:02 | 5 | 2026-05-14 05:02 | 2026-05-14 05:09 | 7 | 12 | Planned UPS replacement activity | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Ghulam
318 | Sirti-WAN-R3-Ticket-290 | NA | 2026-05-14 | P029C2-ENC05-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa planned shutdown |  | Zone 38 | 25.281278° 51.503972° | Inside Doha | P2 - High | 2026-05-14 08:00 | 2026-05-14 08:03 | 3 | 2026-05-14 08:17 | 2026-05-14 09:46 | 89.1 | 106.25 | Kahramaa planned shutdown, FLM installed temporary PG to restore devices | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Hicham
319 | Sirti-WAN-R3-Ticket-291 | NA | 2026-05-14 | DUK-DBR-UPE-01 DUK-DBR-USG-01 DUK-DBR-USG-02 | Adel | Power Modules stopped working | power alarm | UPS DB-03 Main breaker was tripped at DUK-DBR |  | Zone 80 | 25.3775425 51.22843816 | Outside Doha | P3 - Medium | 2026-05-14 09:55 | 2026-05-14 09:59 | 3.95 | 2026-05-14 10:40 | 2026-05-14 10:42 | 2.2833 | 47.2333 | FLM switched on tripped main CB at UPS DB-03 at DUK-DBR | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hicham
320 | Sirti-WAN-R3-Ticket-291 | NA | 2026-05-14 | P004-MOQ-CE-01 | Adel | link down | LAN Link Down | UPS DB-03 Main breaker was tripped at DUK-DBR |  | Zone 51 | 25°22'39.2 N 51°13'42.0 E | Outside Doha | P3 - Medium | 2026-05-14 09:55 | 2026-05-14 09:59 | 4.0167 | 2026-05-14 10:40 | 2026-05-14 10:47 | 6.9833 | 52 | FLM switched on tripped main CB at UPS DB-03 at DUK-DBR | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hicham
321 | Sirti-WAN-R3-Ticket-292 | NA | 2026-05-14 | P005-ENC412-CE-01 | Adel | system power lower than the threshold | End device power alarm | ADAM6060 module is not communication properly which is connected to port 1/2 |  | Zone 51 | 25.3203266° 51.4472961° | Outside Doha | P3 - Medium | 2026-05-14 09:40 | 2026-05-14 09:42 | 2.0667 | 2026-05-14 10:30 | 2026-05-14 10:35 | 5 | 55.0667 | No fault detected from WAN/switch side. Investigation confirmed the alarm is related to the ADAM-6060 module connected on Gi1/2, which showed repeated PoE detect/disconnect events and is currently offline with no MAC address or LLDP neighbor detected. Switch PSU and environmental status are healthy. Also, the ADAM-6060 module is externally powered, therefore no fault has been identified from WAN/switch side. | Completed | Non-maintainer | 3rd party | 3rd party | Alarm Cleared | Hicham
322 | Sirti-WAN-R3-Ticket-293 | NA | 2026-05-14 | P010-ENC01-UPE01 | Sanket | CPU Temperature too high | High Temperature | AC is not cooling |  | Zone 81 | 25.139881, 51.407393 | Outside Doha | P3 - Medium | 2026-05-14 15:58 | 2026-05-14 16:04 | 6.1667 | 2026-05-14 16:06 | 2026-05-14 16:08 | 1.6667 | 9.8333 | Alarm Auto restored before FLM reached the site | Completed | Non-maintainer | Defect | AC | Alarm Cleared | -
323 | Sirti-WAN-R3-Ticket-294 | NA | 2026-05-14 | P029C2-ENC05-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa planned shutdown |  | Zone 38 | 25.281278° 51.503972° | Inside Doha | P2 - High | 2026-05-14 16:38 | 2026-05-14 16:40 | 2.3333 | 2026-05-14 16:41 | 2026-05-14 17:04 | 22.1 | 25.4333 | Kahramaa planned shutdown, FLM switched temporary PG to Kahramaa | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Salem Haj
324 | Sirti-WAN-R3-Ticket-295 | NA | 2026-05-14 | P006-ENC02-UPE-01 P006-ENC02-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-14 18:03 | 2026-05-14 18:05 | 2 | 2026-05-14 18:07 | 2026-05-14 18:08 | 1.1667 | 5 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
325 | Sirti-WAN-R3-Ticket-296 | NA | 2026-05-15 | P023C1-ENC01-CE-01 | Adel | link down | LAN Link Down | no power at LAN cabinet ENC07 |  | Zone 90 | 25.111748° 51.583897° | Outside Doha | P3 - Medium | 2026-05-15 10:03 | 2026-05-15 10:07 | 4 | 2026-05-15 10:50 | 2026-05-15 13:46 | 175.95 | 222.5167 | FLM switchon on CB at LAN ENC07 | Completed | Non-maintainer | N/a | N/a | Alarm Cleared | Najeeb
326 | Sirti-WAN-R3-Ticket-297 | NA | 2026-05-15 | P012-ENC82-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 57 | 25.1917451° 51.4552041 | Outside Doha | P2 - High | 2026-05-15 15:13 | 2026-05-15 15:18 | 5.15 | 2026-05-15 15:20 | 2026-05-15 15:21 | 0.91667 | 8.1167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
327 | Sirti-WAN-R3-Ticket-297 | NA | 2026-05-15 | P006-ENC17-UPE-02 P006-ENC17-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-05-15 23:17 | 2026-05-15 23:22 | 5.1 | 2026-05-15 23:22 | 2026-05-15 23:23 | 1.4833 | 6.5833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
328 | Sirti-WAN-R3-Ticket-298 | NA | 2026-05-16 | 22FEB-ENC25-UPE-02 (100GE 1/0/1) 22FEB-ENC01-UPE-01 (100GE 1/0/1) P003-TCR-NPE-01 (100GE 1/3/0/5) P003-TCR-NPE-01 (100GE 2/3/0/5) DWDM Links Down (P003_To_RMC_S P060_Pri P003_To_RMC_P SOC_P003-P015 Pri RMC_TO_P060_TO_RAA_S P060_Sec RMC_TO_P003_S_TO_P015_S SOC_TO_P060_RAA_Pri) | Abubaker | Link Down | WAN Link Down | QNBN Planned Activity |  | Zone 51 Zone 43 Zone 66 | 25.31832397° 51.47088144° 25.2453756° 51.5148756° 25.3730597 51.5247872 | Outside Doha | P3 - Medium | 2026-05-16 01:01 | 2026-05-16 01:06 | 5.1667 | 2026-05-16 01:06 | 2026-05-16 04:39 | 213.3167 | 218.4833 | Planned QNBN Activity | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
329 | Sirti-WAN-R3-Ticket-299 | NA | 2026-05-16 | DUK-ENC12-UPE-02 | Adel | Temperature higher than Upper threshold | High Temperature | AC02 compressor is found faulty |  | Zone 80 | 25.4302156° 51.1497491° | Outside Doha | P3 - Medium | 2026-05-16 12:12 | 2026-05-16 12:14 | 2 | 2026-05-16 15:28 | 2026-05-16 15:30 | 2.5833 | 198.3833 | AC2, the old compressor was removed, condenser and evaporator flushed with nitrogen, cleaned with a vacuum pump, a new 80Ufd capacitor installed, 134A gas refilled, temperature set, and parts cleaned. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
330 | Sirti-WAN-R3-Ticket-300 | NA | 2026-05-16 | P019-ENC15-UPE-01 | Adel | Temperature higher than Upper threshold | High Temperature | Gas leakage and Compressor power cable found faulty |  | Zone 55 | 25.442833° 51.223831° | Outside Doha | P3 - Medium | 2026-05-16 12:01 | 2026-05-16 12:05 | 4 | 2026-05-16 12:21 | 2026-05-16 13:22 | 61.2667 | 81.0167 | Faulty power cable on the compressor was identified and replaced; additionally, a leak was fixed and thorough cleaning was carried out. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
331 | Sirti-WAN-R3-Ticket-301 | NA | 2026-05-16 | RAA-ENC01-CE-01 | Adel | Link down | LAN Link Down | link auto restored |  | Zone 27 | 25.284123° 51.5558539° | Inside Doha | P3 - Medium | 2026-05-16 12:32 | 2026-05-16 12:36 | 4 | 2026-05-16 12:36 | 2026-05-16 12:42 | 5.9833 | 9.9833 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
332 | Sirti-WAN-R3-Ticket-302 | NA | 2026-05-16 | SAL-ENC20-CE-01 | Adel | Link down | LAN Link Down | link auto restored |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-05-16 13:49 | 2026-05-16 13:50 | 1 | 2026-05-16 13:50 | 2026-05-16 13:51 | 1.0833 | 2.0833 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
333 | Sirti-WAN-R3-Ticket-303 | NA | 2026-05-16 | P010-ENC01-UPE01 | Adel | Temperature higher than Upper threshold | High Temperature | The A/C comperessor is not working properly |  | Zone 81 | 25.139881, 51.407393 | Outside Doha | P3 - Medium | 2026-05-16 14:24 | 2026-05-16 14:26 | 2 | 2026-05-16 15:01 | 2026-05-16 15:06 | 4.7833 | 41.5167 | Adjusted the temperature setting to 30°C; compressor started operating and cooling resumed. Checked compressor load and found it slightly high, then adjusted the refrigerant gas pressure accordingly. Monitored system operation and confirmed the compressor is now functioning properly. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric / Ghulam
334 | Sirti-WAN-R3-Ticket-304 | NA | 2026-05-16 | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P2 - High | 2026-05-16 15:28 | 2026-05-16 15:30 | 2.6667 | 2026-05-16 15:30 | 2026-05-16 15:35 | 5.0167 | 7.6833 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
335 | Sirti-WAN-R3-Ticket-305 | NA | 2026-05-16 | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 | Aaqib | Power Modules stopped working | Power alarm | No Output from UPS |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-05-16 15:32 | 2026-05-16 15:35 | 3.2 | 2026-05-16 16:00 | 2026-05-16 16:17 | 17.1667 | 45.1833 | No output observed. UPS control settings checked and turned it ON. Alarm cleared | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hassan
336 | Sirti-WAN-R3-Ticket-306 | NA | 2026-05-16 | P010-ENC89-UPE-02 | Adel | Temperature higher than Upper threshold | High Temperature | A/C is not cooling |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | P3 - Medium | 2026-05-16 13:27 | 2026-05-16 13:34 | 6.6833 | 2026-05-16 13:34 | 2026-05-16 13:56 | 21.8167 | 28.5 | Checked AC power supply, voltage, and compressor operation. Compressor was overheating and drawing high current (13A instead of normal 6–7A), confirming compressor failure. Removed faulty compressor and cleaned/flushed condenser and evaporator with nitrogen gas. Performed vacuum cleaning, refilled R22 gas, adjusted temperature settings, and cleaned AC components. Tested unit after servicing; AC cooling performance was restored and operating normally. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
337 | Sirti-WAN-R3-Ticket-307 | NA | 2026-05-17 | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | No power found in Cabinet and FP from Khahrama side |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P2 - High | 2026-05-17 15:47 | 2026-05-17 15:49 | 2.6 | 2026-05-17 16:37 | 2026-05-17 17:47 | 69.65 | 120.3333 | No power in FP, Kharama ticket (Refernece # 261100022460) is created after which power restored. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | khadar
338 | Sirti-WAN-R3-Ticket-308 | NA | 2026-05-17 | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 | Aaqib | Power Modules stopped working | Power alarm | No Output from UPS |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-05-17 17:50 | 2026-05-17 17:51 | 1.7833 | 2026-05-17 17:51 | 2026-05-17 19:29 | 97.5667 | 99.35 | No Output from UPS. Power modules restored after Bypassing UPS | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Maasthan/khadar
339 | Sirti-WAN-R3-Ticket-309 | NA | 2026-05-17 | SAL-ENC20-CE-01 | Aaqib | Link down | LAN Link Down | No power found in LAN Cabinet and FP from Khahrama side |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P3 - Medium | 2026-05-17 15:50 | 2026-05-17 15:51 | 1.5333 | 2026-05-17 17:52 | 2026-05-17 17:56 | 4 | 126.0667 | No power in FP at LAN side, Kharama ticket was created after which power restored. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | khadar
340 | Sirti-WAN-R3-Ticket-310 | NA | 2026-05-17 | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | UPS Planned Bypassing Activity |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P2 - High | 2026-05-17 18:47 | 2026-05-17 18:49 | 2.0333 | 2026-05-17 18:49 | 2026-05-17 19:04 | 14.5667 | 16.6 | Devices were down for bypassing UPS inside cabinet | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Maasthan/khadar
341 | Sirti-WAN-R3-Ticket-311 | NA | 2026-05-17 | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | UPS Planned Bypassing Activity |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P2 - High | 2026-05-17 19:38 | 2026-05-17 19:39 | 0.98333 | 2026-05-17 19:39 | 2026-05-17 19:43 | 4.5167 | 5.5 | Devices were down during bypassing UPS inside cabinet and troubleshooting CE power issue. | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Maasthan/khadar
342 | Sirti-WAN-R3-Ticket-312 | NA | 2026-05-17 | SAL-ENC20-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | UPS Planned Bypassing Activity |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P2 - High | 2026-05-17 19:43 | 2026-05-17 19:43 | 0 | 2026-05-17 19:43 | 2026-05-17 19:46 | 3.0667 | 3.0667 | Devices were down during UPS bypassing and troubleshooting CE power issue. | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Maasthan/khadar
343 | Sirti-WAN-R3-Ticket-313 | NA | 2026-05-18 | P015-ENC80A-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 90 | 25.113315° 51.5735937° | Outside Doha | P2 - High | 2026-05-18 07:52 | 2026-05-18 07:53 | 1 | 2026-05-18 07:53 | 2026-05-18 07:54 | 1.3667 | 2.3667 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
344 | Sirti-WAN-R3-Ticket-314 | NA | 2026-05-18 | DUK-ENC12-CE-01 | Sanket | Link down | LAN Link Down | The link is down towards Local Node (LAN) |  | Zone 80 | 25.4302156° 51.1497491° | Outside Doha | P3 - Medium | 2026-05-18 11:32 | 2026-05-18 11:34 | 2 | 2026-05-18 12:26 | 2026-05-18 12:41 | 15 | 68.85 | The Link is down towards LAN | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Irshad
345 | Sirti-WAN-R3-Ticket-315 | NA | 2026-05-18 | DUK-ENC12-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC02 compressor is found faulty |  | Zone 80 | 25.4302156° 51.1497491° | Outside Doha | P3 - Medium | 2026-05-18 12:38 | 2026-05-18 12:40 | 2.2167 | 2026-05-18 13:18 | 2026-05-18 13:43 | 25 | 65 | The AC breaker tripped because the compressor was faulty. We removed the old compressor and installed a new one. The condenser and evaporator were flushed with nitrogen and vacuumed. A new 80µF capacitor was fitted, R134a refrigerant was filled, and the thermostat temperature was set. Finally, all AC parts were cleaned with a blower and cloth. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | khadar
346 | Sirti-WAN-R3-Ticket-316 | NA | 2026-05-19 | SAL-ENC26-CE-01 | Sanket | Link down | LAN Link Down (25GE 1/0/2) | KAHRAMAA Maintenance activity |  | Zone 82 | 25.1435454° 51.2478413° | Outside Doha | P3 - Medium | 2026-05-19 07:02 | 2026-05-19 07:07 | 5 | 2026-05-19 07:52 | 2026-05-19 09:42 | 109.6 | 159.1667 | KAHRAMAA Maintenance activity, FLM installed temporary PG to restore devices | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Rizwan
347 | Sirti-WAN-R3-Ticket-317 | NA | 2026-05-19 | SAL-ENC26-CE-01 | Sanket | Link down | LAN Link Down (25GE 1/0/3) | KAHRAMAA Maintenance activity |  | Zone 82 | 25.1435454° 51.2478413° | Outside Doha | P3 - Medium | 2026-05-19 07:02 | 2026-05-19 07:07 | 5 | 2026-05-19 07:52 | 2026-05-19 10:59 | 186.6167 | 236.1833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Rizwan
348 | Sirti-WAN-R3-Ticket-318 | NA | 2026-05-19 | P015-ENC80A-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for Power Bypass |  | Zone 90 | 25.113315° 51.5735937° | Outside Doha | P2 - High | 2026-05-19 12:23 | 2026-05-19 12:24 | 1 | 2026-05-19 12:28 | 2026-05-19 12:29 | 1 | 6.6 | Planned activity for Power Bypass | Completed | Non-maintainer | N/a | N/a | Devices Back Online | Najeeb
349 | Sirti-WAN-R3-Ticket-319 | NA | 2026-05-20 | P003-ENC05-CE-01-DGME01 | Abubaker | Link down | LAN Link Down (GE 0/0/3) | LAN switch 1705-SR1-ASW-WI3-01 was not responding |  | Zone 66 | 25.3811922° 51.5208128° | Outside Doha | P3 - Medium | 2026-05-20 01:01 | 2026-05-20 01:11 | 10.4 | 2026-05-20 01:52 | 2026-05-20 02:03 | 10.6167 | 62.1667 | FLM restarted the LAN switch 1705-SR1-ASW-WI3-01 connected to the port GE0/0/3 as the LAN switch was not responding | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Umair
350 | Sirti-WAN-R3-Ticket-320 | NA | 2026-05-20 | P007C2-ENC99-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 54 | 25.2967109° 51.4488814° | Outside Doha | P2 - High | 2026-05-20 04:28 | 2026-05-20 04:32 | 4.1667 | 2026-05-20 04:32 | 2026-05-20 04:33 | 0.75 | 4.9167 | Kahramaa power interruption, the power & device restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Back Online | -
351 | Sirti-WAN-R3-Ticket-321 | NA | 2026-05-20 | P011-ENC55-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | AC breaker was Tripped |  | Zone 49 | 25.2209722° 51.5862222° | Outside Doha | P2 - High | 2026-05-20 07:19 | 2026-05-20 07:22 | 3.1167 | 2026-05-20 08:05 | 2026-05-20 08:13 | 7.95 | 54.1167 | The AC breaker was found in a tripped state. Each time it was switched ON, it immediately tripped again. As a precaution, the AC unit has been isolated and temporarily kept OFF | Completed | Non-maintainer | Defect | AC | Device Back Online | Rizwan
352 | Sirti-WAN-R3-Ticket-322 | NA | 2026-05-20 | SAL-ENC20-CE-01 | Sanket | CRC Error | LAN CRC Error Port GE 1/0/9 | The Ethernet cable has issue |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | P4 - Low | 2026-05-20 09:02 | 2026-05-20 09:05 | 3.3833 | 2026-05-20 09:36 | 2026-05-20 09:47 | 11.0167 | 45.1833 | The Ethernet cable has been replaced | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Hichem
353 | Sirti-WAN-R3-Ticket-323 | NA | 2026-05-20 | RMC-ENC-SSW-02 | Sanket | CRC Error | WAN CRC Error Port 40GE 1/1/0/0 | SFP Issue |  | Zone 58 | 25.2410344° 51.4752267° | Outside Doha | P4 - Low | 2026-05-20 11:35 | 2026-05-20 11:37 | 2 | 2026-05-20 11:40 | 2026-05-20 12:57 | 77.3667 | 81.75 | SFP module replaced at RMC-ENC-SSW-02, port 40GE 1/1/0/0 | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Arfa
354 | Sirti-WAN-R3-Ticket-324 | NA | 2026-05-21 | P028C2-ENC01-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | ITS FP breaker tripped (Cable Burn) |  | Zone 7 | 25.283910° 51.5496128° | Inside Doha | P2 - High | 2026-05-21 07:20 | 2026-05-21 07:25 | 4.5 | 2026-05-21 07:54 | 2026-05-21 08:25 | 31.3667 | 64.85 | The ITS feeder pillar main breaker was tripping repeatedly. When the FLM attempted to switch it ON, it turned OFF immediately. A temporary PG was installed to restore the devices. Further inspection of the ITS feeder pillar main cable identified a burnt section causing the short circuit and breaker tripping. The damaged cable section was removed, re-terminated with proper lugs, and reconnected to the breaker. | Completed | Maintainer | N/a | N/a | Device Back Online | Rizwan
355 | Sirti-WAN-R3-Ticket-325 | NA | 2026-05-21 | RAA-ENC01-UPE-01 | Sanket | Link Down | WAN link down (100GE 1/0/0 and 100GE 1/0/1) | Attenuator issues |  | Zone 48 | 25.284123° 51.5558539° | Outside Doha | P3 - Medium | 2026-05-21 07:07 | 2026-05-21 07:16 | 8.65 | 2026-05-21 07:48 | 2026-05-21 08:27 | 39.2167 | 80.1333 | The attenuators in the link were faulty. We replaced them and added new 5dB attenuators. The links are now restored. | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Hichem
356 | Sirti-WAN-R3-Ticket-326 | NA | 2026-05-21 | P040-CPE01-ENC01-DSW | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The ROMD inspection (Ashghal Team) |  | Zone 48 | 25.284123° 51.5558539° | Outside Doha | P2 - High | 2026-05-21 07:07 | 2026-05-21 07:16 | 8.65 | 2026-05-21 07:48 | 2026-05-21 09:31 | 102.9333 | 143.85 | The ROMD inspection (Ashghal Team) | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Device Back Online | -
357 | Sirti-WAN-R3-Ticket-327 | NA | 2026-05-21 | P028C2-ENC01-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | ITS FP breaker tripped (Cable Burn) |  | Zone 7 | 25.283910° 51.5496128° | Inside Doha | P2 - High | 2026-05-21 09:48 | 2026-05-21 09:49 | 1 | 2026-05-21 09:49 | 2026-05-21 09:53 | 3.6333 | 4.6333 | The ITS feeder pillar main breaker was tripping repeatedly. When the FLM attempted to switch it ON, it turned OFF immediately. A temporary PG was installed to restore the devices. Further inspection of the ITS feeder pillar main cable identified a burnt section causing the short circuit and breaker tripping. The damaged cable section was removed, re-terminated with proper lugs, and reconnected to the breaker. | Completed | Maintainer | N/a | N/a | Device Back Online | Rizwan
358 | Sirti-WAN-R3-Ticket-328 | NA | 2026-05-21 | CRR-ENC26-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 25 | 25.2675° 51.5259° | Inside Doha | P2 - High | 2026-05-21 10:08 | 2026-05-21 10:10 | 2.5 | 2026-05-21 10:41 | 2026-05-21 10:42 | 1.3833 | 34.4333 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Back Online | Rizwan
359 | Sirti-WAN-R3-Ticket-329 | NA | 2026-05-21 | P002-ENC14-UPE-02 | Sanket | Temperature higher than Upper threshold | High Temperature | AC is not cooling |  | Zone 55 | 25.249° 51.471° | Outside Doha | P3 - Medium | 2026-05-21 11:47 | 2026-05-21 11:51 | 4.7 | 2026-05-21 12:17 | 2026-05-21 12:19 | 1.9333 | 32.2167 | Replaced the faulty 40+5 µF dual run capacitor and copper filter drier, and repaired the refrigerant leak at the compressor line. The AC unit was thoroughly cleaned and tested after completion of the work. Cooling performance is now normal, and the AC system is operating properly. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hichem
360 | Sirti-WAN-R3-Ticket-330 | NA | 2026-05-21 | P002-ENC14-UPE-02 P002-ENC14-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | While Trouble shooting the AC issue , CB is tripped |  | Zone 55 | 25.249° 51.471° | Outside Doha | P2 - High | 2026-05-21 13:07 | 2026-05-21 13:08 | 1.1 | 2026-05-21 13:10 | 2026-05-21 13:13 | 3 | 6.1 | While Trouble shooting the AC issue , CB is tripped | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan
361 | Sirti-WAN-R3-Ticket-331 | NA | 2026-05-21 | DUK-ENC06-CE-01 | Aaqib | Link Down | LAN Link down | Link Flapping and high ping delay/ intermittent due to cable bend |  | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | P3 - Medium | 2026-05-21 16:14 | 2026-05-21 16:25 | 10.35 | 2026-05-21 18:14 | 2026-05-21 18:19 | 5.2667 | 124.35 | Cable was forn bend and tight, Issue resolve after rerouting UTP cable. | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | AbuTahir
362 | Sirti-WAN-R3-Ticket-332 | NA | 2026-05-22 | P005-TCR-CE-01 P005-TCR-CE-02 | Abubaker | Link Down | LAN Link down | The links P005-TCR-CE-01 (GE 1/0/13) P005-TCR-CE-02 (GE 1/0/13) were down from tunnel access switch side |  | Zone 51 | 25.3199307 51.447548 | Outside Doha | P3 - Medium | 2026-05-22 02:38 | 2026-05-22 02:48 | 9.6167 | 2026-05-22 02:48 | 2026-05-22 06:03 | 194.8 | 204.4167 | Issue has been escalated to the tunnel team and they confirmed that the Linkshare down due to some fiber troubleshooting activity by tunnel team, Links restored after activity completed | Completed | Non-maintainer | 3rd Party | Tunnel Control Room Team (P005) | Alarm Cleared | -
363 | Sirti-WAN-R3-Ticket-333 | NA | 2026-05-22 | P011-ENC44-UPE-02 | Sanket | Power Modules stopped working | Power Modules stopped working | PWR1 stopped working |  | Zone 50 | 25.22292 51.57976 | Outside Doha | P3 - Medium | 2026-05-22 09:29 | 2026-05-22 09:32 | 3.5333 | 2026-05-22 09:48 | 2026-05-22 09:48 | 0.35 | 19.3333 | Kahramaa power interruption, the power module restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
364 | Sirti-WAN-R3-Ticket-334 | NA | 2026-05-23 | DUK-ENC06-CE-01 | Sanket | Link Down | LAN Link down | Link Flapping |  | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | P3 - Medium | 2026-05-23 14:24 | 2026-05-23 14:26 | 2 | 2026-05-23 14:52 | 2026-05-23 14:55 | 3.45 | 31 | FLM replaced Ethernet cable and checked POE power connections | Completed | Maintainer | NA | N/a | Alarm Cleared | Khadar
365 | Sirti-WAN-R3-Ticket-335 | NA | 2026-05-24 | COR-ENC07-CE-01 | Aaqib | Link Down | LAN Link down | Link Auto Restored |  | Zone 63 | 25.311996° 51.520188° | Outside Doha | P3 - Medium | 2026-05-24 10:21 | 2026-05-24 10:22 | 1.5667 | 2026-05-24 10:22 | 2026-05-24 10:24 | 2.2 | 3.7667 | Link Auto restored after 3 min. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
366 | Sirti-WAN-R3-Ticket-336 | NA | 2026-05-24 | P059C1-Enc04-UPE-01 P059C1-Enc04-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage |  | Zone 71 | 25.3653937° 51.4467471° | Outside Doha | P2 - High | 2026-05-24 11:19 | 2026-05-24 11:22 | 3.25 | 2026-05-24 11:22 | 2026-05-24 11:25 | 2.75 | 6 | khahrama Power Interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Back Online | -
367 | Sirti-WAN-R3-Ticket-337 | NA | 2026-05-24 | P007C2-ENC99-UPE-02 | Aaqib | CPU Temperature too high | High Temperature | AC not cooling, high temp |  | Zone 54 | 25.2967109° 51.4488814° | Outside Doha | P3 - Medium | 2026-05-24 13:24 | 2026-05-24 13:28 | 4 | 2026-05-24 14:23 | 2026-05-24 14:47 | 23.8 | 83.3833 | The faulty copper filter drier-15 was replaced due to a detected leak. The leak was repaired, the filter was replaced, and cleaning was completed as part of the maintenance work. AC is replaced with another AC unit. After testing, the air conditioning system was confirmed to be operating normally with proper cooling performance. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
368 | Sirti-WAN-R3-Ticket-338 | NA | 2026-05-25 | P023C2-ENC11-UPE-01 P023C2-ENC11-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down |  | Zone 53 | 25.325262° , 51.329176° | Outside Doha | P2 - High | 2026-05-25 05:21 | 2026-05-25 05:27 | 5.5833 | 2026-05-25 05:27 | 2026-05-25 05:37 | 10.0833 | 15.6667 | Kahramaa power interruption, Devices restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
369 | Sirti-WAN-R3-Ticket-338 | NA | 2026-05-25 | P023C3-ENC21-UPE-01 P023C3-ENC21-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down |  | Zone 55 | 25.1750987° 51.3316767° | Outside Doha | P2 - High | 2026-05-25 05:21 | 2026-05-25 05:27 | 5.65 | 2026-05-25 05:27 | 2026-05-25 05:37 | 10.2333 | 15.8833 | Kahramaa power interruption, Devices restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
370 | Sirti-WAN-R3-Ticket-390 | NA | 2026-05-25 | P005-ENC413-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | No Output from UPS |  | Zone 52 | 25.3203738° 51.4518769° | Outside Doha | P2 - High | 2026-05-25 12:39 | 2026-05-25 12:42 | 3.1167 | 2026-05-25 13:36 | 2026-05-25 14:39 | 63.8 | 120.2833 | UPS was not giving output. Device restored after bypassing UPS. | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Irshad
371 | Sirti-WAN-R3-Ticket-340 | NA | 2026-05-25 | P007 SOC_TO_TCC_P004 Sec | Abubaker | HARD_ERR | Equipment Error | Hardware error alarm on the Universal 100Gbit/s Line Service Processing Board |  | Zone 52 | 25.2942202° 51.4657002° | Outside Doha | P4 - Low | 2026-05-25 23:49 | 2026-05-26 | 10.8667 | 2026-05-26 | 2026-05-26 00:05 | 4.7667 | 15.6333 | Performed a cold reset for the board Z5UNS4 | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
372 | Sirti-WAN-R3-Ticket-341 | NA | 2026-05-26 | P007C2-ENC99-CE-01 P007C2-ENC99-UPE-02 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down |  | Zone 54 | 25.2967109° 51.4488814° | Outside Doha | P2 - High | 2026-05-26 02:23 | 2026-05-26 02:34 | 11.4667 | 2026-05-26 02:34 | 2026-05-26 02:40 | 6.0333 | 17.5 | Kahramaa power interruption, Devices restored once the power recovered | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
373 | Sirti-WAN-R3-Ticket-342 | NA | 2026-05-27 | P023C2-ENC11-UPE-01 P023C2-ENC11-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down |  | Zone 53 | 25.325262° , 51.329176° | Outside Doha | P2 - High | 2026-05-27 06:41 | 2026-05-27 06:44 | 3.3 | 2026-05-27 06:44 | 2026-05-27 08:02 | 77.3333 | 80.6333 | Kahramaa power interruption. Devices restored just FLM arrival to site. No action required by FLM | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
374 | Sirti-WAN-R3-Ticket-342 | NA | 2026-05-27 | P023C3-ENC21-UPE-01 P023C3-ENC21-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down |  | Zone 55 | 25.1750987° 51.3316767° | Outside Doha | P2 - High | 2026-05-27 06:41 | 2026-05-27 06:44 | 3.3 | 2026-05-27 06:44 | 2026-05-27 08:02 | 77.3333 | 80.6333 | Kahramaa power interruption. Devices restored just FLM arrival to site. No action required by FLM | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
375 | Sirti-WAN-R3-Ticket-343 | NA | 2026-05-27 | RAA-ENC01-CE-01 | Aaqib | Link Down | LAN Link down | LAN device was down due to high temperature |  | Zone 27 | 25.284123° 51.5558539° | Inside Doha | P3 - Medium | 2026-05-27 12:01 | 2026-05-27 12:07 | 6.0333 | 2026-05-27 12:32 | 2026-05-27 12:36 | 4.0667 | 35.1 | The 10G Link is conneceted to LAN device and the LAN device was down due to high temperature inside cabinet. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Patrick
376 | Sirti-WAN-R3-Ticket-344 | NA | 2026-05-27 | RAA-ENC01-UPE-01 | Aaqib | CPU Temperature too high | High Temperature | A/C is not cooling |  | Zone 27 | 25.284123° 51.5558539° | Inside Doha | P3 - Medium | 2026-05-27 12:06 | 2026-05-27 12:07 | 1.4667 | 2026-05-27 12:35 | 2026-05-27 12:36 | 1.0667 | 30.5333 | AC Team replaced comperossor relay , AC is working normally now | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
377 | Sirti-WAN-R3-Ticket-345 | NA | 2026-05-27 | P011-ENC44-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is not cooling |  | Zone 50 | 25.22292 51.57976 | Outside Doha | P3 - Medium | 2026-05-27 13:09 | 2026-05-27 13:14 | 4.55 | 2026-05-27 13:51 | 2026-05-27 13:59 | 7.5 | 49.55 | AC Team Maintaned the AC and restart it , now it is working and keeping under observation | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
378 | Sirti-WAN-R3-Ticket-346 | NA | 2026-05-27 | P017C2-ENC01-CE-01 | Aaqib | Link Down | LAN Link down | Ethernet cable faulty |  | Zone 57 | 25.1702778° 51.4710278° | Outside Doha | P3 - Medium | 2026-05-27 13:32 | 2026-05-27 13:39 | 7.1167 | 2026-05-27 13:32 | 2026-05-27 14:40 | 67.8 | 67.8 | FLM replaced Ethernet cable connected to CE port GE1/1 | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | -
379 | Sirti-WAN-R3-Ticket-347 | NA | 2026-05-27 | 22FEB-ENC01-CE-01 | Adel | Link Down | LAN Link down | Link is down due to QNBN fiber damage |  | Zone 43 | 25.2453756° 51.5148756° | Outside Doha | P3 - Medium | 2026-05-27 19:41 | 2026-05-27 19:45 | 4 | 2026-05-27 20:23 | 2026-05-28 16:39 | 1216.35 | 1258.2333 | Issue scalated to QNBN team, QNBN team shifted the link to a healthy fiber and the link recovered | Completed | Non-maintainer | 3rd Party | QNBN Fiber | Link is Up | Khadar
380 | Sirti-WAN-R3-Ticket-348 | NA | 2026-05-28 | CRR-ENC30-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is not cooling |  | Zone 24 | 25.268° 51.515° | Inside Doha | P3 - Medium | 2026-05-28 13:02 | 2026-05-28 13:06 | 4.4167 | 2026-05-28 14:50 | 2026-05-28 14:52 | 2.0333 | 109.85 | FLM team fill the R22 refrigrator gas and perform general servicing for the A/C system | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
381 | Sirti-WAN-R3-Ticket-349 | NA | 2026-05-28 | P028C2-ENC25-UPE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | High Temperature inside the Cabinet and A/C compressor not working properly |  | Zone 13 | 25.2898333° 51.5151388° | Inside Doha | P3 - Medium | 2026-05-28 13:06 | 2026-05-28 13:10 | 3.6 | 2026-05-28 13:27 | 2026-05-28 13:30 | 3.2 | 24.05 | alarm auto cleared however the FLM team fixed the malfunctioning compressor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
382 | Sirti-WAN-R3-Ticket-350 | NA | 2026-05-28 | P007C2-ENC01-UPE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | Alarm Auto restored before FLM reached the site |  | Zone 38 | 25.2931613° 51.4894255° | Inside Doha | P3 - Medium | 2026-05-28 13:30 | 2026-05-28 13:33 | 3.4833 | 2026-05-28 13:24 | 2026-05-28 13:48 | 23.1667 | 17.8167 | we found the condenser pipe was leaking. The unit was opened and cleaned with chemicals and water. The copper condenser pipe was repaired by brazing, and a leakage test was done using nitrogen gas. Next, the condenser and evaporator were flushed with nitrogen gas and cleaned with chemicals. The AC parts were washed with water, serviced with a blower, and wiped with cloth towels. A vacuum pump was used to clean the system. We then filled the AC with R‑407C refrigerant gas, set the temperature, and cleaned the parts again with a blower and cloth towels. | Completed | Non-maintainer | Defect | AC | Alarm auto Cleared | Khadar
383 | Sirti-WAN-R3-Ticket-351 | NA | 2026-05-28 | P007C2-ENC01-UPE-01 | Aaqib | Power Modules stopped working | Power alarm | Kharahma Outage is down |  | Zone 38 | 25.2931613° 51.4894255° | Inside Doha | P3 - Medium | 2026-05-28 14:45 | 2026-05-28 14:51 | 6.4167 | 2026-05-28 14:45 | 2026-05-28 16:28 | 103.4167 | 103.4167 | Kahramaa power interruption, alarms cleared once the power recovered | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
384 | Sirti-WAN-R3-Ticket-351 | NA | 2026-05-28 | P007C2-ENC01-UPE-01 P007C2-ENC01-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down |  | Zone 38 | 25.2931613° 51.4894255° | Inside Doha | P2 - High | 2026-05-28 14:45 | 2026-05-28 14:51 | 5.6167 | 2026-05-28 14:45 | 2026-05-28 15:24 | 38.1667 | 38.1667 | Kahramaa power interruption, alarms cleared once the power recovered | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
385 | Sirti-WAN-R3-Ticket-352 | NA | 2026-05-28 | P007C7P2-ENC26-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down |  | Zone 52 | 25.3062231° 51.4645491° | Outside Doha | P2 - High | 2026-05-28 17:49 | 2026-05-28 17:51 | 2.1333 | 2026-05-28 17:49 | 2026-05-28 17:58 | 9.2 | 9.2 | Kahramaa power interruption, alarms cleared once the power recovered | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
386 | Sirti-WAN-R3-Ticket-352 | NA | 2026-05-28 | P007C7P2-ENC49-CE-01 | Abubaker | Link Down | WAN Link down | Kharahma Outage is down |  | Zone 52 | 25.3133081° 51.4633077° | Outside Doha | P3 - Medium | 2026-05-28 17:48 | 2026-05-28 17:58 | 9.65 | 2026-05-28 17:49 | 2026-05-28 18:41 | 52.0167 | 52.5333 | Link auto restored, checked the link health and ensured that the link is up and optical power level is OK and cleared the alarm manually | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
387 | Sirti-WAN-R3-Ticket-353 | NA | 2026-05-29 | P019-ENC63-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | While performing PPM activity, the device got shut down |  | Zone 73 | 25.5878055° 51.1144722° | Outside Doha | P2 - High | 2026-05-29 01:58 | 2026-05-29 01:59 | 1 | 2026-05-29 01:59 | 2026-05-29 02:02 | 2.9333 | 3.9333 | Device went down during PPM actvity | Completed | Non-maintainer | Planned Activity | PPM | Devices Back Online | Ghulam
388 | Sirti-WAN-R3-Ticket-354 | NA | 2026-05-29 | RAA-ENC01-UPE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C was found off |  | Zone 27 | 25.284123° 51.5558539° | Inside Doha | P3 - Medium | 2026-05-29 10:36 | 2026-05-29 10:41 | 5.4 | 2026-05-29 11:22 | 2026-05-29 11:26 | 3.9667 | 50.15 | AC starts cooling after restarting | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Irshad
389 | Sirti-WAN-R3-Ticket-355 | NA | 2026-05-29 | P011-ENC44-UPE-02 | Abubaker | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling |  | Zone 50 | 25.22292 51.57976 | Outside Doha | P3 - Medium | 2026-05-29 10:52 | 2026-05-29 10:59 | 6.9 | 2026-05-29 10:52 | 2026-05-29 11:52 | 59.7667 | 59.7667 | Alarm Cleared before FLM reach the site however FLM team went to the site and restarted the A/C and compressor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Abuthahir
390 | Sirti-WAN-R3-Ticket-356 | NA | 2026-05-29 | P023C3-Enc21-UPE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | 2 A/Cs are working but not cooling |  | Zone 55 | 25.1750987° 51.3316767° | Outside Doha | P3 - Medium | 2026-05-29 12:07 | 2026-05-29 12:12 | 4.75 | 2026-05-29 13:03 | 2026-05-29 13:06 | 2.7667 | 58.3 | FLM opened the cabinet door and kept it open for a while to cool down the cabinet and clear the alarms and scheduled for A/C inspection and servicing | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Najeeb
391 | Sirti-WAN-R3-Ticket-357 | NA | 2026-05-29 | P003-ENC40-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling |  | Zone 65 | 25.3344995° 51.5180512° | Outside Doha | P3 - Medium | 2026-05-29 12:07 | 2026-05-29 12:14 | 6.4333 | 2026-05-29 12:58 | 2026-05-29 13:00 | 1.9333 | 52.7333 | FLM opened the cabinet door and kept it open for a while to cool down the cabinet and clear the alarms and scheduled for A/C inspection and servicing | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
392 | Sirti-WAN-R3-Ticket-358 | NA | 2026-05-29 | 22FEB-ENC25-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling |  | Zone 51 | 25.31832397, 51.47088144 | Outside Doha | P3 - Medium | 2026-05-29 12:07 | 2026-05-29 12:12 | 4.5333 | 2026-05-29 12:07 | 2026-05-29 13:16 | 68.4333 | 68.4333 | Alarm Cleared before FLM reach the site however FLM team went to the site and restarted the A/C and compressor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
393 | Sirti-WAN-R3-Ticket-359 | NA | 2026-05-29 | P008C3-ENC01-UPE-01 | Aaqib | CPU Temperature too high | High Temperature | Schema Under Salam Tech |  | Zone 55 | 25.2614822° 51.4801647° | Outside Doha | P3 - Medium | 2026-05-29 13:32 | 2026-05-29 13:36 | 4.5333 | 2026-05-29 13:32 | 2026-05-29 15:37 | 125.5 | 125.5 | Schema Under Salam Tech. Escalated to there team | Completed | Non-maintainer | 3rd Party | Salam Tech | Alarm Cleared | -
394 | Sirti-WAN-R3-Ticket-360 | NA | 2026-05-29 | P010-ENC89-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | P3 - Medium | 2026-05-29 14:50 | 2026-05-29 14:52 | 2.8833 | 2026-05-29 15:28 | 2026-05-29 16:26 | 57.5667 | 96.0667 | Inspected the AC unit by checking the power cables and voltage supply, then cleaned the system thoroughly. Restarted the AC power and performed a general service. After servicing, the unit was tested and confirmed to be operating properly with good cooling performance, and the compressor is now functioning correctly and providing cooling as expected | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham / Khadar
395 | Sirti-WAN-R3-Ticket-361 | NA | 2026-05-29 | P006-ENC02-UPE-01 P006-ENC02-UPE-02 | Abubaker | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling |  | Zone 56 | 25.2190399° 51.4369501° | Outside Doha | P3 - Medium | 2026-05-29 15:10 | 2026-05-29 15:16 | 6.3167 | 2026-05-29 15:10 | 2026-05-29 16:47 | 97.35 | 97.35 | Inspected the AC unit by checking the power cables and voltage supply, and found that the AC compressor was not responding. Restarted the AC power and carried out a general service. After servicing, the unit was tested and confirmed to be working properly with good cooling performance. The AC compressor is now functioning properly | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
396 | Sirti-WAN-R3-Ticket-362 | NA | 2026-05-30 | P060-ENC125-CE-GME-01 | Sanket/Adel | Communication betweeen NMS and NE is Abnormal | Device Down | No power at WAN cabinet |  | Zone 70 | 25.639484° 51.491537° | Outside Doha | P2 - High | 2026-05-30 06:07 | 2026-05-30 06:13 | 5.2 | 2026-05-30 06:57 | 2026-05-30 08:47 | 110 | 159.6167 | FLM connected portable generator temporary till they find the FP location , then FLM switched on tripped CB at FP | Completed | Maintainer | N/a | N/a | Devices Back Online | Hicham
397 | Sirti-WAN-R3-Ticket-363 | NA | 2026-05-30 | SAL-ENC63-CE-01 | Sanket | Link Down | LAN Link down | Link auto restored (GE 1/0/9 towards Local Node) |  | Zone 96 | 24.8301249° , 50.8705931° | Outside Doha | P3 - Medium | 2026-05-30 23:21 | 2026-05-30 23:28 | 7.1 | 2026-05-30 23:49 | 2026-05-30 23:50 | 1 | 29.3167 | Alarm Auto restored before FLM reached the site (The Link is down towards LAN) | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | -
398 | Sirti-WAN-R3-Ticket-364 | NA | 2026-05-31 | P060-ENC179-UPE-02 P060-ENC179-CE-GME-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | While performing PPM activity, the device got shut down |  | Zone 70 | 25.63950 51.49451 | Outside Doha | P2 - High | 2026-05-31 01:01 | 2026-05-31 01:02 | 1 | 2026-05-31 01:03 | 2026-05-31 01:06 | 2.5167 | 4.5167 | While performing PPM activity, the device got shut down | Completed | Non-maintainer | Planned Activity | PPM | Devices Back Online | Ghulam
399 | Sirti-WAN-R3-Ticket-365 | NA | 2026-05-31 | P060-ENC179-UPE-02 P060-ENC179-CE-GME-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | During the PPM activity at site P060-ENC179, it was observed that the main power cable lugs require proper tightening and fixing |  | Zone 70 | 25.63950 51.49451 | Outside Doha | P2 - High | 2026-05-31 02:07 | 2026-05-31 02:08 | 1 | 2026-05-31 02:14 | 2026-05-31 02:15 | 0.81667 | 7.8333 | During the PPM activity at site P060-ENC17, it was observed that the main power cable lugs require proper tightening and fixing.Then, we removed the main power cable, installed the cable lugs, fixed them properly | Completed | Non-maintainer | Planned Activity | PPM | Devices Back Online | Ghulam
400 | Sirti-WAN-R3-Ticket-366 | NA | 2026-05-31 | P003-ENC05-CE-01-DGME01 | Sanket | Link Down | LAN Link down | Fiber Patch chord issue at Port XG 0/1/7 towards 17025-SR1-ASW-E12-10 |  | Zone 66 | 25.3811922° 51.5208128° | Outside Doha | P3 - Medium | 2026-05-31 04:40 | 2026-05-31 04:50 | 10.0833 | 2026-05-31 05:33 | 2026-05-31 06:11 | 37.55 | 91.1667 | Verified that the LC/PC-to-LC/PC 3-meter fiber patch cord was faulty. Replaced it with a new fiber patch cord, and the link is now up and stable | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Umair
401 | Sirti-WAN-R3-Ticket-371 | NA | 2026-05-31 | P011-ENC44-UPE-02 | Adel | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling |  | Zone 50 | 25.22292 51.57976 | Outside Doha | P3 - Medium | 2026-05-31 13:49 | 2026-05-31 13:52 | 3 | 2026-05-31 14:31 | 2026-05-31 14:34 | 3.1833 | 45.1833 | FLM team went to the site and restarted the A/C and compressor then the cabinet Temp become normal and then replaced the 40+5 capacitor. The unit is now operating normally and performing well | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar / Eric
402 | Sirti-WAN-R3-Ticket-372 | NA | 2026-05-31 | P006-ENC17-CE-01 | Abubaker | Link Down | WAN link down | Ethernet loose connection for the port port Gi 0/0/12 |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P3 - Medium | 2026-05-31 18:32 | 2026-05-31 18:41 | 9.3167 | 2026-05-31 20:22 | 2026-05-31 20:24 | 2.1833 | 112.0667 | Cleaned the Ethernet cable and connected it properly to the switch port Gi 0/0/12 | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Hassan
403 | Sirti-WAN-R3-Ticket-373 | NA | 2026-06-01 | P040-CPE01-ENC01-DSW | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | ITSQ activity on site |  | Zone 48 | 25.284123° 51.5558539° | Outside Doha | P2 - High | 2026-06-01 08:59 | 2026-06-01 09:04 | 5 | 2026-06-01 09:30 | 2026-06-01 09:39 | 8.8833 | 39.6833 | issue is escalated to ITSQ via mail , FLM visisted and found ITSQ team is working at cabinet | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Alarm Cleared | Hicham
404 | Sirti-WAN-R3-Ticket-374 | NA | 2026-06-01 | P003-ENC40-UPE-02 | Adel | power module stopped working | power alarm | kahromaa power inturruption |  | Zone 65 | 25.3344995° 51.5180512° | Outside Doha | P3 - Medium | 2026-06-01 10:22 | 2026-06-01 10:26 | 4 | 2026-06-01 11:30 | 2026-06-01 11:49 | 19 | 87.5 | Kahromaa power inturruption alarm is auto restored , flm did not visit in summer time | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
405 | Sirti-WAN-R3-Ticket-375 | NA | 2026-06-01 | P028C2-ENC-07-CE-01.omc.local | Adel | link down | LAN Link down | LAN switch was found down due to breaker tripped |  | Zone 27 | 25.2827572° 51.5448455° | Inside Doha | P3 - Medium | 2026-06-01 09:57 | 2026-06-01 10:03 | 6 | 2026-06-01 16:34 | 2026-06-01 16:42 | 8.2 | 404.5167 | breaker turned ON and power is restored, the LAN switch become up and link restored | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Irshad
406 | Sirti-WAN-R3-Ticket-376 | NA | 2026-06-01 | P059C1-ENC04-CE-01 P059C1-ENC04-UPE-01 | Adel | optical model temprature too high | High Temperature | A/C is fans are not working, Temprature is high inside the cabinet |  | Zone 71 | 25.3653937° 51.4467471° | Outside Doha | P3 - Medium | 2026-06-01 13:04 | 2026-06-01 13:06 | 2 | 2026-06-01 16:30 | 2026-06-01 16:31 | 1.2 | 207.5667 | General servicing of both AC units was carried out, including cleaning and inspection of filters and coils. After completion of service, both AC units were started and tested.Both AC units are now operating normally with proper cooling performance. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Najeeb
407 | Sirti-WAN-R3-Ticket-377 | NA | 2026-06-01 | P006-ENC02-UPE-01 | Adel | CPU Temperature too high | High Temperature | Compressor faulty |  | Zone 56 | 25.2190399° 51.4369501° | Outside Doha | P3 - Medium | 2026-06-01 13:56 | 2026-06-01 13:58 | 3 | 2026-06-01 16:06 | 2026-06-01 16:12 | 5.5667 | 136.2333 | The faulty AC compressor at cabinet P06-ENC-02 was replaced with a new LG unit, the condenser and evaporator were thoroughly cleaned, new filter, capillary pipe, and capacitor were installed, R-22 gas was charged, and after servicing, the AC was tested and confirmed to be cooling properly. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Sanjeewa
408 | Sirti-WAN-R3-Ticket-378 | NA | 2026-06-01 | DUK-ENC04-CE-01 | Abubaker | Link Down | LAN link down | Port Auto restored before FLM reach the site |  | Zone 58 | 25.3809325° 51.2215135° | Outside Doha | P3 - Medium | 2026-06-01 16:40 | 2026-06-01 16:50 | 10.3667 | 2026-06-01 16:40 | 2026-06-01 16:57 | 17.6667 | 17.6667 | Link Auto restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
409 | Sirti-WAN-R3-Ticket-379 | NA | 2026-06-01 | DUK-ENC30-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power inturruption |  | Zone 85 | 25.4637854° 50.930279° | Outside Doha | P2 - High | 2026-06-01 20:57 | 2026-06-01 21:01 | 4.1 | 2026-06-01 20:57 | 2026-06-01 21:04 | 7.5833 | 7.5833 | Kahromaa power inturruption device flapped and auto restored before FLM reaching the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Back Online | -
410 | Sirti-WAN-R3-Ticket-380 | NA | 2026-06-02 | P003-ENC05-CE-01-DGME01 | Aaqib | Link Down | LAN link down | SFP was stuck and was not functioning |  | Zone 69 | 25.3811922° 51.5208128° | Outside Doha | P3 - Medium | 2026-06-02 00:30 | 2026-06-02 00:33 | 3.4 | 2026-06-02 01:17 | 2026-06-02 01:39 | 21.25 | 68.8667 | SFP was stuck. Link was restored after JIJO at LAN switch side. | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Hassan
411 | Sirti-WAN-R3-Ticket-381 | NA | 2026-06-02 | P028C2-ENC07-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | MCB was found tripped |  | Zone 6 | 25.2827572° 51.5448455° | Inside Doha | P2 - High | 2026-06-02 02:25 | 2026-06-02 02:29 | 4.45 | 2026-06-02 03:09 | 2026-06-02 03:18 | 9 | 53.4167 | Device restored after turning ON MCB inside cabinet | Completed | Non-maintainer | Environmental | Heat summer | Device Back Online | Hichem
412 | Sirti-WAN-R3-Ticket-382 | NA | 2026-06-02 | P003-ENC05-CE-01-DGME01 | Aaqib | Link Down | LAN link down | Dirty UPC connector causing Link down |  | Zone 69 | 25.3811922° 51.5208128° | Outside Doha | P3 - Medium | 2026-06-02 03:19 | 2026-06-02 03:22 | 2.3833 | 2026-06-02 04:23 | 2026-06-02 04:36 | 13.2167 | 76.7167 | The fiber connector was dirty. Team cleaned it and reinserted the connector. After which the link restored. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Umair
413 | Sirti-WAN-R3-Ticket-383 | NA | 2026-06-02 | DUK-ENC04-CE-01 | Aaqib | Link Down | LAN link down | RJ45 Connector was dirty and cable not propelry routed |  | Zone 58 | 25.3809325° 51.2215135° | Outside Doha | P3 - Medium | 2026-06-02 04:43 | 2026-06-02 04:53 | 9.8333 | 2026-06-02 05:26 | 2026-06-02 05:41 | 15.6167 | 57.8833 | Connector was dirty. Team just plug out, clean it and reroute and insert again after which link restored | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Ghulam
414 | Sirti-WAN-R3-Ticket-384 | NA | 2026-06-02 | P059C1-ENC20-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | No power at WAN cabinet |  | Zone 70 | 25.44194931° 51.41112813° | Outside Doha | P2 - High | 2026-06-02 09:37 | 2026-06-02 09:40 | 3 | 2026-06-02 16:44 | 2026-06-02 17:27 | 43.3833 | 469.9 | FLM switched on tripped CB at FP | Completed | Non-maintainer | Environmental | Heat summer | Device Back Online | Sanjeewa
415 | Sirti-WAN-R3-Ticket-385 | NA | 2026-06-02 | P003-ENC40-UPE-02 | Adel | CRC Error alarm notification | CRC Alarm on port 2/0/0 | errors oncounted on port |  | Zone 65 | 25.3344995° 51.5180512° | Outside Doha | P4 - Low | 2026-06-02 14:50 | 2026-06-02 14:55 | 5 | 2026-06-02 15:40 | 2026-06-02 16:09 | 28.9333 | 78.6 | FLM replaced ER SFP at IE5000-6009 port TE1/26 | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Najeeb
416 | Sirti-WAN-R3-Ticket-386 | NA | 2026-06-03 | P007-ENC-NMS-SW-01 | Adel | Link Down | Link Down to UPS | Planned activity with huawei team for UPS PPM inside battery room |  | Zone 52 | 25.2942202° 51.4657002° | Outside Doha | P3 - Medium | 2026-06-03 08:52 | 2026-06-03 08:53 | 1 | 2026-06-03 08:52 | 2026-06-03 08:58 | 6.2 | 6.2 | Planned activity with huawei team for UPS PPM inside battery room | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | Patric
417 | Sirti-WAN-R3-Ticket-387 | NA | 2026-06-03 | P011-ENC44-UPE-02 | Sanket | Power module stopped working | Power module powered off | Loose connectivity of Cable at PWR1 |  | Zone 50 | 25.22292 51.57976 | Outside Doha | P3 - Medium | 2026-06-03 15:52 | 2026-06-03 15:55 | 3.6667 | 2026-06-03 16:32 | 2026-06-03 16:33 | 1.3333 | 41.6667 | All loose connections were tightened, and voltage levels were checked. Alarm LEDs on the module were inspected, and no signs of overheating were observed | Completed | maintainer | N/a | N/a | Alarm Cleared | Najeeb
418 | Sirti-WAN-R3-Ticket-388 | NA | 2026-06-04 | COR-ENC12-CE-01 | Adel | Link Down | LAN link down | LAN link XGE 0/0/4 towards BSW 6009 is down. BSW- Cisco switch was hanged |  | Zone 63 | 25.324005699251956, 51.52792742883553 | Outside Doha | P3 - Medium | 2026-06-04 14:27 | 2026-06-04 14:33 | 6 | 2026-06-04 15:16 | 2026-06-04 15:22 | 5.9333 | 54.9 | Visited the site, checked the power cables and voltage, then restarted the switch. The nodes came back online | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Khadar
419 | Sirti-WAN-R3-Ticket-389 | NA | 2026-06-04 | COR-ENC12-CE-01 | Sanket | Link Down | LAN link down | LAN link XGE 0/0/4 towards BSW 6009 is down. BSW- Cisco switch was hanged |  | Zone 63 | 25.324005699251956, 51.52792742883553 | Outside Doha | P3 - Medium | 2026-06-04 17:46 | 2026-06-04 17:48 | 1.4333 | 2026-06-04 18:05 | 2026-06-04 18:09 | 4.7333 | 23.05 | Visited the site, checked the power cables and voltage, then restarted the switch. The nodes came back online | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Khadar
420 | Sirti-WAN-R3-Ticket-390 | NA | 2026-06-04 | COR-ENC12-CE-01 | Sanket | Link Down | LAN link down | LAN link XGE 0/0/4 towards BSW 6009 is down. BSW- Cisco Switch is Faulty |  | Zone 63 | 25.324005699251956, 51.52792742883553 | Outside Doha | P3 - Medium | 2026-06-04 21:18 | 2026-06-04 21:21 | 3.1167 | 2026-06-04 21:23 | 2026-06-05 01:18 | 234.9833 | 240.1 | Faulty switch ( Cisco IE4000 ) switch was replaced with a Cisco IE3500 switch. | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Khadar
421 | Sirti-WAN-R3-Ticket-391 | NA | 2026-06-06 | P015-SS1-USG-01 | Sanket | OSPF Down | OSPF neighbours Status changed fluctuating (LAN) | Comnet switch meisbehaving |  | Zone 91 | 25.146674° 51.5765472° | Outside Doha | P4 - Low | 2026-06-06 21:40 | 2026-06-06 21:52 | 12.3667 | 2026-06-06 22:30 | 2026-06-07 18:33 | 1202.6333 | 1253 | The continous fluctuation in SCATS. The LAN (CommNet) switch was experiencing issues, so we rebooted it. | Completed | Non-maintainer | 3rd Party | N/a | Alarm Cleared | Irshad, Khadar, Rizwan
422 | Sirti-WAN-R3-Ticket-392 | NA | 2026-06-07 | P001-ENC32-CE-01 P001-ENC32-UPE-02 P001-ENC30-CE-04 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power inturruption |  | Zone 49 | 25.2351561° 51.5844811° | Outside Doha | P2 - High | 2026-06-07 10:35 | 2026-06-07 10:38 | 3 | 2026-06-07 10:35 | 2026-06-07 10:41 | 5.9167 | 5.9167 | kahromaa power inturruption /Alarm auto cleared | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
423 | Sirti-WAN-R3-Ticket-393 | NA | 2026-06-08 | P015-SS1-USG-01 | Adel | Link Down | LAN link down | as per tunnel operator , power issue on Tunnel core switches |  | Zone 91 | 25.146674° 51.5765472° | Outside Doha | P3 - Medium | 2026-06-08 07:06 | 2026-06-08 07:07 | 1.6833 | 2026-06-08 07:06 | 2026-06-08 07:10 | 4.6833 | 4.6833 | Issue resolved after rebooting SS3 and SS1 at P015 tunnel which falls under RF001 and resolve the issue | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Hichem
424 | Sirti-WAN-R3-Ticket-394 | NA | 2026-06-08 | DUK-ENC04-CE-01 | Adel | Link Down | LAN link down | Planned PPM activity on site |  | Zone 58 | 25.3809325° 51.2215135° | Outside Doha | P3 - Medium | 2026-06-08 08:30 | 2026-06-08 08:32 | 2 | 2026-06-08 08:30 | 2026-06-08 08:36 | 6.4167 | 6.4167 | During Planned PPM activity on site , link flapped | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | Farooq
425 | Sirti-WAN-R3-Ticket-395 | NA | 2026-06-08 | P008C3-ENC01-UPE-01 | AMR | CPU temperature too High | High Temperature | Temperature issue in the Cabinet |  | Zone 55 | 25.2614822° 51.4801647° | Outside Doha | P3 - Medium | 2026-06-08 13:33 | 2026-06-08 13:40 | 7 | 2026-06-08 13:40 | 2026-06-08 14:36 | 55.6667 | 62.6667 | The AC temperature issue autoresolved. The schema maintained by Salam Tech | Completed | Non-maintainer | 3rd Party | Salam Tech | Alarm Cleared | -
426 | Sirti-WAN-R3-Ticket-396 | NA | 2026-06-08 | P012-ENC82-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned PPM activity on site |  | Zone 57 | 25.1917451° 51.4552041° | Outside Doha | P2 - High | 2026-06-08 20:38 | 2026-06-08 20:40 | 2.2 | 2026-06-08 20:40 | 2026-06-08 20:42 | 1.4 | 3.6 | While performing PPM activity, the device got shut down | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | Khadar
427 | Sirti-WAN-R3-Ticket-397 | NA | 2026-06-08 | SAL-ENC14-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 55 | 25.1858801° 51.3628538° | Outside Doha | P2 - High | 2026-06-08 20:45 | 2026-06-08 20:46 | 1.0833 | 2026-06-08 20:46 | 2026-06-08 20:47 | 1.0333 | 2.1167 | kahromaa power inturruption /Alarm auto cleared | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
428 | Sirti-WAN-R3-Ticket-398 | NA | 2026-06-09 | SAL-ENC32-CE-01 | Abubaker | Link Down | Remote Collector Link Down | Ports GE1/0/6 Port GE1/0/7 toward remote collector was down |  | Zone 82 | 25.1165799° 51.1812367° | Outside Doha | P3 - Medium | 2026-06-09 03:43 | 2026-06-09 03:50 | 6.6667 | 2026-06-09 03:43 | 2026-06-09 04:24 | 40.3167 | 40.3167 | Link Auto restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
429 | Sirti-WAN-R3-Ticket-399 | NA | 2026-06-09 | 22FEB-ENC25-CE-01 | Adel | Optical module temp is too high | High Temperature | Both AC not working |  | Zone 51 | 25.31832397, 51.47088144 | Outside Doha | P3 - Medium | 2026-06-09 14:10 | 2026-06-09 14:13 | 3 | 2026-06-09 15:43 | 2026-06-09 15:46 | 2.3 | 95.85 | FLM replacaced faulty comprossor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Farooq
430 | Sirti-WAN-R3-Ticket-400 | NA | 2026-06-09 | P061-ENC13-CE-01 | Adel | Optical module temp is too high | High Temperature | Both A/Cs are working but not cooling |  | Zone 55 | 25.263460° 51.459387 | Outside Doha | P3 - Medium | 2026-06-09 14:06 | 2026-06-09 14:09 | 2.9833 | 2026-06-09 15:36 | 2026-06-09 15:52 | 15.8333 | 106.1333 | Electrical inspection was completed for both AC units. It was found that AC Unit #1 had low refrigerant gas and AC Unit #2 had a faulty relay. The refrigerant was refilled, the faulty relay was replaced, and general servicing was carried out on both units, including cleaning of the coils and condensers. After maintenance, both units were tested and confirmed to be operating normally with proper cooling performance. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar / Rizwan
431 | Sirti-WAN-R3-Ticket-401 | NA | 2026-06-09 | SAl-ENC26-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 82 | 25.1435454° 51.2478413° | Outside Doha | P2 - High | 2026-06-09 18:26 | 2026-06-09 18:28 | 2.3667 | 2026-06-09 18:26 | 2026-06-09 18:31 | 4.9 | 4.9 | khahrama Power Interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
432 | Sirti-WAN-R3-Ticket-402 | NA | 2026-06-10 | SAl-ENC56-CE-01 | Adel | Optical module temp is too high | High Temperature | AC outdoor fan was not working |  | Zone 96 | 24.8911735° 50.938318° | Outside Doha | P3 - Medium | 2026-06-10 11:44 | 2026-06-10 11:48 | 4 | 2026-06-10 16:16 | 2026-06-10 16:20 | 3.8 | 275.7833 | AC outdoor fan was not working, then restarted the AC Breaker then AC start working in normal condition. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
433 | Sirti-WAN-R3-Ticket-403 | NA | 2026-06-10 | DUK-ENC04-CE-01 | Adel | Optical module temp is too high | High Temperature | A/C not cooling due to faulty condenser fan |  | Zone 58 | 25.3809325° 51.2215135° | Outside Doha | P3 - Medium | 2026-06-10 12:53 | 2026-06-10 12:56 | 3 | 2026-06-10 16:40 | 2026-06-10 16:48 | 7.4667 | 235.25 | The AC unit was removed from the enclosure cabinet, and the faulty condenser fan was replaced with a new one. The condenser and evaporator coils were chemically cleaned and serviced using water, a blower, and cloth towels. The AC unit was reinstalled in the cabinet, and the temperature was set on the thermostat. All AC parts were cleaned, and the unit was tested. Cooling performance was confirmed to be normal, and the system is operating properly. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
434 | Sirti-WAN-R3-Ticket-404 | NA | 2026-06-10 | SAL-ENC45-CE-01 | Adel | Optical module temp is too high | High Temperature | The AC need to be Fix |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-06-10 12:50 | 2026-06-10 12:55 | 5 | 2026-06-10 15:35 | 2026-06-10 15:37 | 2.35 | 166.8 | The faulty parts has been replaced | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
435 | Sirti-WAN-R3-Ticket-405 | NA | 2026-06-10 | DC23-ENC101-CE-01 | Adel | Optical module temp is too high | High Temperature | A/C not cooling, Damaged wiring, a faulty capacitor, high current on the condenser fan, and a refrigerant gas leak. |  | Zone 51 | 25.3204° 51.470367° | Outside Doha | P3 - Medium | 2026-06-10 12:45 | 2026-06-10 12:50 | 4.7 | 2026-06-10 15:57 | 2026-06-10 16:00 | 2.8333 | 194.6167 | A full inspection of the AC system was carried out, including electrical components, compressor, wiring, condenser fan, and refrigerant circuit. The wiring was repaired, the capacitor and condenser fan were replaced, and the gas leak was repaired. The condenser and evaporator coils were chemically cleaned, and complete AC servicing, flushing, and vacuuming were performed. The unit was tested and confirmed to be operating normally. Cooling performance is normal, and the site is stable. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
436 | Sirti-WAN-R3-Ticket-406 | NA | 2026-06-10 | P008C2-ENC17-CE-01 | Aaqib | Link Down | LAN Link down | MCB was tripped inside LAN Cabinet |  | Zone 56 | 25.2323811° 51.5173691° | Outside Doha | P3 - Medium | 2026-06-10 14:43 | 2026-06-10 14:49 | 6.4667 | 2026-06-10 14:44 | 2026-06-10 14:47 | 2.7833 | 4.4833 | MCB was tripped at LAN cabinet | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
437 | Sirti-WAN-R3-Ticket-407 | NA | 2026-06-10 | P004-Enc43-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | Thermostat settings was not OK |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-06-10 15:17 | 2026-06-10 15:22 | 5.1667 | 2026-06-10 15:29 | 2026-06-10 15:33 | 4.2 | 15.85 | Team Visited the site, checked power cables and voltage, restarted the AC, adjusted the temperature on the thermostat, and now the unit is cooling and working properly. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
438 | Sirti-WAN-R3-Ticket-408 | NA | 2026-06-10 | SAL-ENC45-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device went down during AC troubleshooting activity |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P2 - High | 2026-06-10 16:01 | 2026-06-10 16:03 | 1.9333 | 2026-06-10 16:01 | 2026-06-10 16:03 | 2.2 | 2.2 | Device went down during AC troubleshooting activity | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Abutahir
439 | Sirti-WAN-R3-Ticket-409 | NA | 2026-06-10 | P008C2-ENC33-CE-01 | Aaqib | Link Down | LAN Link down | LAN Link down |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P3 - Medium | 2026-06-10 15:45 | 2026-06-10 15:48 | 3 | 2026-06-10 16:45 | 2026-06-10 16:51 | 6 | 66 | Cisco SW hanged due to high temperature after rebooting node came back online | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared
440 | Sirti-WAN-R3-Ticket-410 | NA | 2026-06-10 | P040-CPE01-ENC01-DSW | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Interruption |  | Zone 48 | 25.284123° 51.5558539° | Outside Doha | P2 - High | 2026-06-10 16:13 | 2026-06-10 16:15 | 1.6167 | 2026-06-10 16:13 | 2026-06-10 16:19 | 5.6 | 5.6 | khahrama Power Interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored
441 | Sirti-WAN-R3-Ticket-411 | NA | 2026-06-10 | P007C2-ENC59-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | UPS power failure, and the AC unit breaker was off |  | Zone 54 | 25.2922123° 51.4648447° | Outside Doha | P2 - High | 2026-06-10 17:34 | 2026-06-10 17:37 | 2.7167 | 2026-06-10 18:20 | 2026-06-10 18:39 | 18.4333 | 64.7667 | After resetting the UPS, the node came back up and the AC unit started working | Completed | Non-maintainer | Defect | UPS | Device Restored | Sanjeewa
442 | Sirti-WAN-R3-Ticket-412 | NA | 2026-06-10 | P008C2-ENC33-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device went down during AC troubleshooting activity |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P2 - High | 2026-06-10 18:07 | 2026-06-10 18:10 | 2.8 | 2026-06-10 18:07 | 2026-06-10 18:17 | 9.7333 | 9.7333 | Device went down during AC troubleshooting activity and turning ON AC breaker | Completed | Non-maintainer | AC defect | AC defect | Device Restored
443 | Sirti-WAN-R3-Ticket-413 | NA | 2026-06-10 | SAL-ENC20-UPE-02 SAL-ENC20-CE-02 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Interruption |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P2 - High | 2026-06-10 19:45 | 2026-06-10 19:47 | 2.2833 | 2026-06-10 19:45 | 2026-06-10 19:50 | 5.6833 | 5.6833 | khahrama Power Interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored
444 | Sirti-WAN-R3-Ticket-414 | NA | 2026-06-10 | DUK-ENC04-CE-01 | Aaqib | Power Module stopped working | Power Modules stopped working | Ongoing AC rectification |  | Zone 58 | 25.3809325° 51.2215135° | Outside Doha | P3 - Medium | 2026-06-10 20:51 | 2026-06-10 20:52 | 0.55 | 2026-06-10 20:51 | 2026-06-10 21:17 | 25.9833 | 25.9833 | No free socket in Cabinet. Power1 removed for AC FAN and compressor changing | Completed | Non-maintainer | Defect | AC | Device Restored | Khadar
445 | Sirti-WAN-R3-Ticket-415 | NA | 2026-06-11 | P008C2-ENC17-CE-01 | Abubaker | Link Down | LAN Link down | LAN Link Port Gi 1/15 towards LAN |  | Zone 56 | 25.2323811° 51.5173691° | Outside Doha | P3 - Medium | 2026-06-11 01:39 | 2026-06-11 01:50 | 10.9 | 2026-06-11 02:14 | 2026-06-11 02:34 | 20.0667 | 54.9667 | LAN SW hanged due to high temperature after rebooting port become Up | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Hassan
446 | Sirti-WAN-R3-Ticket-416 | NA | 2026-06-11 | P005-TCR-CE-02 | Abubaker | Link Down | LAN Link down | LAN Link Down Port Te 1/0/13 towards LAN |  | Zone 51 | 25.3199307 51.447548 | Outside Doha | P3 - Medium | 2026-06-11 03:06 | 2026-06-11 03:13 | 6.6167 | 2026-06-11 03:56 | 2026-06-11 05:39 | 102.9833 | 152.6 | After unplugging and plugging the SFP back in, the link returned to normal. The link is down towards LAN (Tunnel) | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Hicham
447 | Sirti-WAN-R3-Ticket-417 | NA | 2026-06-11 | P008C2-ENC17-CE-01 | Abubaker | Link Down | LAN Link down | LAN Link Port Gi 1/15 towards LAN |  | Zone 56 | 25.2323811° 51.5173691° | Outside Doha | P3 - Medium | 2026-06-11 04:00 | 2026-06-11 04:01 | 0.78333 | 2026-06-11 04:50 | 2026-06-11 04:58 | 8 | 57.7833 | LAN SW hanged due to high temperature after rebooting port become Up | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Ghulam
448 | Sirti-WAN-R3-Ticket-418 | NA | 2026-06-11 | P008C2-ENC17-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Device went down during AC troubleshooting activity |  | Zone 56 | 25.2323811° 51.5173691° | Outside Doha | P2 - High | 2026-06-11 04:52 | 2026-06-11 04:57 | 4.7833 | 2026-06-11 04:52 | 2026-06-11 04:58 | 5.5167 | 5.5167 | Device went down during AC troubleshooting activity | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Ghulam
449 | Sirti-WAN-R3-Ticket-419 | NA | 2026-06-11 | SAL-ENC04-CE-01 | Abubaker | Link Down | LAN Link down | Ports GE 1/0/7 & GE 1/0/6 are down |  | Zone 57 | 25.2204517° 51.4230388° | Outside Doha | P3 - Medium | 2026-06-11 05:02 | 2026-06-11 05:12 | 9.7333 | 2026-06-11 05:02 | 2026-06-11 05:13 | 10.9 | 10.9 | Auto restored before FLM reaching the site | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | -
450 | Sirti-WAN-R3-Ticket-420 | NA | 2026-06-11 | SAL-ENC04-CE-01 | Abubaker | Link Down | LAN Link down | Ports GE 1/0/7 & GE 1/0/6 are down |  | Zone 57 | 25.2204517° 51.4230388° | Outside Doha | P3 - Medium | 2026-06-11 05:26 | 2026-06-11 05:35 | 9.4833 | 2026-06-11 05:26 | 2026-06-11 06:25 | 59.8333 | 59.8333 | Auto restored before FLM reaching the site | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | -
451 | Sirti-WAN-R3-Ticket-421 | NA | 2026-06-11 | P008C2-ENC33-CE-01 | Sanket | Link Down | LAN Link down | LAN Link Port Gi 1/19 towards P008-C2-(33)-N8-R1-USW9-UP57 node is down |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P3 - Medium | 2026-06-11 09:04 | 2026-06-11 09:10 | 6.0667 | 2026-06-11 09:45 | 2026-06-11 10:18 | 33.1667 | 74.2333 | Upon arrival, the node was observed to be overheating, which resulted in the main breaker tripping. The same issue esclated to AC | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Umar
452 | Sirti-WAN-R3-Ticket-422 | NA | 2026-06-11 | P008C2-ENC33-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | AC is not working, AC breaker was found in the OFF position |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P2 - High | 2026-06-11 10:00 | 2026-06-11 10:03 | 3.2833 | 2026-06-11 10:03 | 2026-06-11 10:18 | 15.1667 | 18.45 | Upon arrival, the node was observed to be overheating, which resulted in the main breaker tripping. The same issue esclated to AC | Completed | Non-maintainer | AC defect | AC defect | Device Restored | Umar
453 | Sirti-WAN-R3-Ticket-423 | NA | 2026-06-11 | P008C2-ENC17-CE-01 | Sanket | Link Down | LAN Link down | Devices were down due to overheating |  | Zone 56 | 25.2323811° 51.5173691° | Outside Doha | P3 - Medium | 2026-06-11 10:34 | 2026-06-11 10:38 | 4.2 | 2026-06-11 15:48 | 2026-06-11 16:06 | 18.4 | 332.2167 | Devices were down due to overheating | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
454 | Sirti-WAN-R3-Ticket-424 | NA | 2026-06-11 | P008C2-ENC33-CE-01 | Sanket | Link Down | LAN Link down | LAN Link Port Gi 1/19 towards P008-C2-(33)-N8-R1-USW9-UP57 node is down |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P3 - Medium | 2026-06-11 10:49 | 2026-06-11 10:50 | 1.1667 | 2026-06-11 16:12 | 2026-06-11 16:26 | 13.9667 | 337.0667 | Devices were down due to overheating | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
455 | Sirti-WAN-R3-Ticket-425 | NA | 2026-06-11 | P008C2-ENC33-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | AC is not working and devices are overheated |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P2 - High | 2026-06-11 15:33 | 2026-06-11 15:36 | 3.1 | 2026-06-11 15:33 | 2026-06-11 15:39 | 6.3 | 6.3 | AC is not working and devices are overheated | Completed | Non-maintainer | AC defect | AC defect | Device Restored | Irshad
456 | Sirti-WAN-R3-Ticket-426 | NA | 2026-06-11 | P005-TCR-CE-02 | Aaqib | Link Down | LAN Link down | Port TE 1/0/13 is down |  | Zone 51 | 25.3199307 51.447548 | Outside Doha | P3 - Medium | 2026-06-11 15:30 | 2026-06-11 15:34 | 3.7 | 2026-06-11 17:19 | 2026-06-11 17:32 | 13.1667 | 121.6167 | Escalated to P005 control room team | Completed | Non-maintainer | 3rd Party | Tunnel | Alarm Cleared
457 | Sirti-WAN-R3-Ticket-427 | NA | 2026-06-11 | P008C2-ENC17-CE-01 | Aaqib | Link Down | LAN Link down | Connected to LAN switch. AC team is working on site |  | Zone 56 | 25.2323811° 51.5173691° | Outside Doha | P3 - Medium | 2026-06-11 16:21 | 2026-06-11 16:27 | 5.1167 | 2026-06-11 16:21 | 2026-06-11 16:29 | 7.5833 | 7.5833 | Connected to LAN switch. AC team is working on site | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Najeeb/Irshad
458 | Sirti-WAN-R3-Ticket-428 | NA | 2026-06-11 | P008C2-ENC33-CE-01 | Aaqib | Link Down | LAN Link down | Link connected to LAN switch which was down during switch trouleshooting |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P3 - Medium | 2026-06-11 16:28 | 2026-06-11 16:30 | 1.4833 | 2026-06-11 16:28 | 2026-06-11 18:15 | 106.25 | 106.25 | Link connected to LAN switch which was down during switch trouleshooting. Faulty LAN switch replaced | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Najeeb/Irshad
459 | Sirti-WAN-R3-Ticket-429 | NA | 2026-06-11 | P008C2-ENC17-CE-01 | Aaqib | Link Down | LAN Link down | Link connected to LAN and that LAN switch was hanging intermittently |  | Zone 56 | 25.2323811° 51.5173691° | Outside Doha | P3 - Medium | 2026-06-11 16:32 | 2026-06-11 16:35 | 2.4667 | 2026-06-11 16:32 | 2026-06-11 20:31 | 239.0333 | 239.0333 | Link connected to LAN switch which was down during switch trouleshooting. Faulty LAN switch replaced | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Masthan Basha
460 | Sirti-WAN-R3-Ticket-430 | NA | 2026-06-11 | P008C2-ENC33-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device was down during LAN switch fault rectification |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P2 - High | 2026-06-11 16:38 | 2026-06-11 16:40 | 2.8667 | 2026-06-11 16:38 | 2026-06-11 16:48 | 9.8667 | 9.8667 | Device was down during LAN switch fault rectification | Completed | Non-maintainer | Planned Activity | N/a | Device Restored | Najeeb/Irshad
461 | Sirti-WAN-R3-Ticket-431 | NA | 2026-06-11 | P008C2-ENC33-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device was down during LAN switch fault rectification |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P2 - High | 2026-06-11 18:29 | 2026-06-11 18:29 | 0.55 | 2026-06-11 18:29 | 2026-06-11 18:37 | 7.6167 | 7.6167 | team is working on site for LAN switch fault rectification | Completed | Non-maintainer | Planned Activity | N/a | Device Restored | Najeeb/Irshad
462 | Sirti-WAN-R3-Ticket-432 | NA | 2026-06-11 | 22FEB-ENC25-CE-01 | Aaqib | Link Down | LAN Link down | No Power at LAN Cabinet |  | Zone 51 | 25.31832397, 51.47088144 | Outside Doha | P3 - Medium | 2026-06-11 21:14 | 2026-06-11 21:18 | 4.2833 | 2026-06-11 21:51 | 2026-06-11 22:24 | 32.5833 | 69.6667 | khahrama Power Interruption towards LAN | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Hassan
463 | Sirti-WAN-R3-Ticket-433 | NA | 2026-06-13 | COR-ENC07-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Power down due to KAHRAMAA planned activity |  | Zone 63 | 25.31320770235765, 51.52089816892454 | Inside Doha | P2 - High | 2026-06-13 01:56 | 2026-06-13 02:09 | 12.7333 | 2026-06-13 03:14 | 2026-06-13 03:41 | 27 | 104.7333 | Power was down due to KAHRAMAA planned activity, FLM team energized the device using power generator | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Umair
464 | Sirti-WAN-R3-Ticket-434 | NA | 2026-06-13 | COR-ENC07-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Device is energized by a power generator and KAHRAMAA Power is back |  | Zone 63 | 25.31320770235765, 51.52089816892454 | Inside Doha | P2 - High | 2026-06-13 05:43 | 2026-06-13 05:44 | 1.1167 | 2026-06-13 05:44 | 2026-06-13 05:49 | 5 | 6.1167 | Disconnected the power generator and connected back KAHRAMAA power source | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Umair
465 | Sirti-WAN-R3-Ticket-435 | NA | 2026-06-13 | SAL-ENC45-CE-01 | Sanket | Link Down | LAN Link down | The Link is down towards LAN (GE 1/0/14) |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-06-13 09:09 | 2026-06-13 09:23 | 14 | 2026-06-13 09:23 | 2026-06-13 09:46 | 23 | 37 | Autorestored. The Link is down towards LAN | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | -
466 | Sirti-WAN-R3-Ticket-436 | NA | 2026-06-13 | DUK-ENC06-CE-01 | Aaqib | Link Down | LAN Link down | Intermittent fluctuation in LAN Link towards (GE 1/0/9) local nodes |  | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | P3 - Medium | 2026-06-13 16:17 | 2026-06-13 16:20 | 3.1 | 2026-06-13 17:12 | 2026-06-13 17:15 | 2.7333 | 57.8333 | Loose URP cable connection | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Irshad
467 | Sirti-WAN-R3-Ticket-437 | NA | 2026-06-14 | P028C2-ENC04-CE-01.omc.local | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 13 | 25.2791625° 51.5290008° | Inside Doha | P2 - High | 2026-06-14 02:20 | 2026-06-14 02:22 | 2 | 2026-06-14 02:20 | 2026-06-14 02:32 | 12.45 | 12.45 | KAHRAMAA Power interruption, the power and device restored before FLM reaching the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
468 | Sirti-WAN-R3-Ticket-438 | NA | 2026-06-14 | P028C2-ENC06-DGME-CE-01.omc.local | Abubaker | Link Down | WAN Link Down | Port Te1/25 WAN Link toward P028C2-ENC04-CE-01 Port Te1/26 is down |  | Zone 13 | 25.2892675° 51.5213447° | Inside Doha | P3 - Medium | 2026-06-14 02:20 | 2026-06-14 02:25 | 4.7667 | 2026-06-14 03:01 | 2026-06-14 03:21 | 19.7833 | 60.55 | Checked the optical power at the ODF, Removed the SFP module for Te1/25 and cleaned the fiber cable and reconnected again the SFP module and fiber cable at P028C2-ENC06-DGME-CE and cleared the alarm on eSight | Completed | Non-Maintainer | node Up | N/a | Alarm Cleared | Hicham
469 | Sirti-WAN-R3-Ticket-439 | NA | 2026-06-14 | IE5000-2302 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 23 | 25.272861° 51.510861° | Inside Doha | P2 - High | 2026-06-14 06:06 | 2026-06-14 06:09 | 2.5 | 2026-06-14 06:06 | 2026-06-14 06:16 | 9.0667 | 9.0667 | KAHRAMAA Power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
470 | Sirti-WAN-R3-Ticket-440 | NA | 2026-06-14 | IE5000-2302 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 23 | 25.272861° 51.510861° | Inside Doha | P2 - High | 2026-06-14 06:27 | 2026-06-14 06:29 | 2.0167 | 2026-06-14 06:27 | 2026-06-14 07:38 | 70.7 | 70.7 | KAHRAMAA Power interruption, FLM connected the power generator to restore the device temporirly. KHARAMAA refrence Number261100028890 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Hicham
471 | Sirti-WAN-R3-Ticket-441 | NA | 2026-06-14 | IE5000-2302 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The temporary generator has been removed because Kahramaa power has been restored |  | Zone 23 | 25.272861° 51.510861° | Inside Doha | P2 - High | 2026-06-14 08:12 | 2026-06-14 08:13 | 1.0667 | 2026-06-14 08:16 | 2026-06-14 08:23 | 7.0333 | 11.15 | The temporary generator has been removed because Kahramaa power has been restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Umair
472 | Sirti-WAN-R3-Ticket-442 | NA | 2026-06-14 | IE5000-2302 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama team working on site |  | Zone 23 | 25.272861° 51.510861° | Inside Doha | P2 - High | 2026-06-14 16:52 | 2026-06-14 16:56 | 3.6 | 2026-06-14 16:52 | 2026-06-14 17:03 | 10.7833 | 10.7833 | KAHRAMAA Power interruption. Main fused busred, Khahram team is working on site. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
473 | Sirti-WAN-R3-Ticket-443 | NA | 2026-06-14 | IE5000-2302 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama team working on site |  | Zone 23 | 25.272861° 51.510861° | Inside Doha | P2 - High | 2026-06-14 17:13 | 2026-06-14 17:16 | 2.85 | 2026-06-14 17:13 | 2026-06-14 17:22 | 9.1833 | 9.1833 | KAHRAMAA Power interruption. Main fused busred, Khahram team is working on site. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
474 | Sirti-WAN-R3-Ticket-444 | NA | 2026-06-15 | SAL-ENC04-CE-01 | Abubaker | Link Down | LAN Link down | Port down interface GE 1/0/10 connected to Local Device |  | Zone 57 | 25.2204517° 51.4230388° | Outside Doha | P3 - Medium | 2026-06-15 02:57 | 2026-06-15 03:03 | 6.0833 | 2026-06-15 03:32 | 2026-06-15 03:43 | 11.5 | 46.1 | The link was down due to maintenance work being carried out by the camera maintenance team. port become up once CCTV team finished the activity and connected back the CCTV cable | Completed | Non-maintainer | 3rd Party | CCTV Contractor | Alarm Cleared | Umair
475 | Sirti-WAN-R3-Ticket-445 | NA | 2026-06-15 | P019-ENC48-CE-01 | Abubaker | Link Down | LAN Link down | Port 25GE 1/0/3 toward LAN is down |  | Zone 73 | 25.589361° 51.112765° | Outside Doha | P3 - Medium | 2026-06-15 04:46 | 2026-06-15 04:47 | 1.05 | 2026-06-15 04:46 | 2026-06-15 04:48 | 1.8167 | 1.8167 | Port went down for less than 2 mins during PPM activity after switching off the A/C for servicing. | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | Ghulam
476 | Sirti-WAN-R3-Ticket-446 | NA | 2026-06-15 | P019-ENC48-CE-01 | Abubaker | Link Down | LAN Link down | Port 25GE 1/0/3 toward LAN is down |  | Zone 73 | 25.589361° 51.112765° | Outside Doha | P3 - Medium | 2026-06-15 04:57 | 2026-06-15 04:58 | 0.51667 | 2026-06-15 04:57 | 2026-06-15 05:02 | 4.4167 | 4.4167 | Noticed that the LAN device get off due to temperature during the A/C PPM activity, FLM switch on the A/C and LAN device become up and port become up | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | Ghulam
477 | Sirti-WAN-R3-Ticket-447 | NA | 2026-06-15 | CRR-ENC26-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 41 | 25.26019° 51.52483° | Inside Doha | P2 - High | 2026-06-15 08:13 | 2026-06-15 08:15 | 2 | 2026-06-15 08:13 | 2026-06-15 08:19 | 5.1333 | 5.1333 | khahrama power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
478 | Sirti-WAN-R3-Ticket-448 | NA | 2026-06-15 | DUK-ENC06-CE-01 | Adel | Link Down | LAN Link down | fluctuation in LAN Link towards (GE 1/0/9) local nodes |  | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | P3 - Medium | 2026-06-15 09:47 | 2026-06-15 09:50 | 3 | 2026-06-15 09:47 | 2026-06-15 10:46 | 59 | 59 | link is auto restored towards local link | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
479 | Sirti-WAN-R3-Ticket-449 | NA | 2026-06-15 | RAA-ENC01-UPE-01 | Adel | Temperature higher than Upper threshold | High Temperature | Relay issue |  | Zone 27 | 25.284123° 51.5558539° | Inside Doha | P3 - Medium | 2026-06-15 10:53 | 2026-06-15 10:55 | 2 | 2026-06-15 10:53 | 2026-06-15 11:34 | 41.15 | 41.15 | The team changed the relay, and the AC is now working normally | Completed | Non-maintainer | AC defect | AC defect | Alarm Cleared | Khadar
480 | Sirti-WAN-R3-Ticket-450 | NA | 2026-06-15 | RAA-ENC01-CE-01 | Adel | LAN Link Down | LAN Link down | Khahroma power inturruption |  | Zone 27 | 25.284123° 51.5558539° | Inside Doha | P3 - Medium | 2026-06-15 10:46 | 2026-06-15 10:50 | 3 | 2026-06-15 10:46 | 2026-06-15 12:59 | 132.3833 | 132.3833 | khahrama power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
481 | Sirti-WAN-R3-Ticket-451 | NA | 2026-06-15 | MV2-ENC-CE-01 MV2-ENC-CE-02 | Adel | LAN Link Down | LAN Link down | The main and redundent links are connected to microsoft switch which is decomissioned |  | Zone 70 | 25.550630° 51.43908° | Outside Doha | P3 - Medium | 2026-06-15 10:25 | 2026-06-15 10:30 | 5 | 2026-06-15 10:25 | 2026-06-15 10:40 | 15.1333 | 15.1333 | Switch decommisioned by Customer | Completed | Non-maintainer | 3rd Party | MV2 Control Room | Alarm Cleared | -
482 | Sirti-WAN-R3-Ticket-452 | NA | 2026-06-15 | P012-ENC117-CE-01 | Sanket | Link Down | LAN Link down | LAN link down port GE 1/18 towards P12-BSW-117-6 |  | Zone 57 | 25.1895779° 51.4471456° | Outside Doha | P3 - Medium | 2026-06-15 17:30 | 2026-06-15 17:31 | 1.0333 | 2026-06-15 17:30 | 2026-06-15 17:32 | 1.95 | 1.95 | The link is down towards LAN and Autorestored. | Completed | Non-maintainer | No Node Down | N/a | Alarm Cleared | -
483 | Sirti-WAN-R3-Ticket-453 | NA | 2026-06-16 | SAl-ENC56-CE-01 | Abubaker | Link Down | LAN Link down | Ports GE1/0/6 & GE1/0/7 Toward the Remote Collector are down |  | Zone 96 | 24.8911735° 50.938318° | Outside Doha | P3 - Medium | 2026-06-16 05:50 | 2026-06-16 05:57 | 7.15 | 2026-06-16 05:50 | 2026-06-16 06:04 | 14.2167 | 14.2167 | Auto restored before FLM reaching the site | Completed | Non-maintainer | No Node Down | N/a | Alarm Cleared | -
484 | Sirti-WAN-R3-Ticket-454 | NA | 2026-06-16 | P012-ENC30-CE-04 | Sanket | Link Down | LAN Link down | link down port GE 1/9 towards LAN |  | Zone 56 | 25.2162349° 51.5021362° | Outside Doha | P3 - Medium | 2026-06-16 13:39 | 2026-06-16 13:40 | 1.1 | 2026-06-16 13:40 | 2026-06-16 13:42 | 1.8333 | 2.9333 | The link is down towards LAN and Autorestored. | Completed | Non-maintainer | No Node Down | N/a | Alarm Cleared
485 | Sirti-WAN-R3-Ticket-455 | NA | 2026-06-16 | SAL-ENC20-UPE-02 SAL-ENC20-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power inturruption |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P2 - High | 2026-06-16 17:03 | 2026-06-16 17:05 | 2 | 2026-06-16 17:03 | 2026-06-16 17:31 | 27.2 | 27.2 | khahrama power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
486 | Sirti-WAN-R3-Ticket-456 | NA | 2026-06-17 | P060-ENC56-CE-DGME-01.omc.local | Abubaker | Link Down | LAN Link down | Interfaces GE1/14 & GE1/13 Toward LAN |  | Zone 69 | 25.4561017° 51.4775073° | Outside Doha | P3 - Medium | 2026-06-17 03:28 | 2026-06-17 03:34 | 6.0833 | 2026-06-17 04:24 | 2026-06-17 07:07 | 163.3 | 219.3833 | Replaced the SFP at P060-ENC56-CE-DGME-01.omc.local port GE1/13 and rebooted the LAN switch | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Eric / Hicham
487 | Sirti-WAN-R3-Ticket-457 | NA | 2026-06-18 | P060-ENC56-CE-DGME-01.omc.local | Abubaker | Link Down | WAN Link down | Link Te1/25 at P028C2-ENC-01-CE-01.omc.local toward Te1/26 at P028C2-ENC-14-CE-01.omc.local is down and optical Rx power was -40 |  | Zone 69 | 25.2839108° 51.5496128° | Outside Doha | P3 - Medium | 2026-06-18 00:11 | 2026-06-18 00:19 | 8.3833 | 2026-06-18 00:49 | 2026-06-18 01:11 | 22.25 | 60.6333 | Replaced the patch cord cables at P028C2-ENC-01-CE-01 (interface Te1/25 | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Rizwan
488 | Sirti-WAN-R3-Ticket-458 | NA | 2026-06-18 | P008C3-ENC01-UPE-01 | Aaqib | CPU temperature too High | High Temperature | High Temperature inside the Cabinet. Schema under Salam Tech |  | Zone 55 | 25.2614822° 51.4801647° | Outside Doha | P3 - Medium | 2026-06-18 13:29 | 2026-06-18 13:36 | 7.7333 | 2026-06-18 13:29 | 2026-06-18 15:36 | 127.1833 | 127.1833 | High Temperature inside the Cabinet. Schema under Salam Tech | Completed | Non-maintainer | AC defect | AC defect ( 3rd party) | Alarm Cleared
489 | Sirti-WAN-R3-Ticket-459 | NA | 2026-06-21 | SAL-ENC45-CE-01 | Sanket | Link Down | LAN Link down | Port 25GE 1/0/4 towards SAL-LAN- Ring 4 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | P3 - Medium | 2026-06-21 06:03 | 2026-06-21 06:05 | 2.05 | 2026-06-21 06:06 | 2026-06-21 06:07 | 0.9 | 4.05 | While performing PPM activity, the link was down | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | Eric
490 | Sirti-WAN-R3-Ticket-460 | NA | 2026-06-21 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | No Output from UPS |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-06-21 12:01 | 2026-06-21 12:05 | 4.4 | 2026-06-21 15:35 | 2026-06-21 16:00 | 24.8 | 238.7667 | There was no output fprom the UPS, FLM team restarted the UPS and device restored and become online | Completed | maintainer | N/a | N/a | Alarm Cleared | Najeeb
491 | Sirti-WAN-R3-Ticket-461 | NA | 2026-06-21 | P008C3-ENC01-UPE-01 | Aaqib | CPU temperature too High | High Temperature | Compressor found faulty |  | Zone 55 | 25.2614822° 51.4801647° | Outside Doha | P3 - Medium | 2026-06-21 10:38 | 2026-06-21 10:41 | 3.7167 | 2026-06-21 15:30 | 2026-06-21 16:38 | 68.2833 | 360.6667 | Compressor already changed, but condenser fan running very slow — fan itself is faulty. Need to replace condenser fan once Mr. Been confirms from supplier, then collect and fit. To avoid same issue later, check compressor and fan together during service. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
492 | Sirti-WAN-R3-Ticket-462 | NA | 2026-06-21 | P010-ENC01-UPE01 | Abubaker | CPU temperature too High | High Temperature | High Temperature alarm Auto cleared before team reching the site |  | Zone 81 | 25.139881, 51.407393 | Outside Doha | P3 - Medium | 2026-06-21 15:50 | 2026-06-21 15:52 | 1.6 | 2026-06-21 15:50 | 2026-06-21 16:09 | 18.1667 | 18.1667 | Auto restored before FLM reaching the site however the FLM team attended and checked all electrical parameters, which were found to be within the normal range. During the inspection, the AC filters were found to be blocked and were cleaned and washed thoroughly.The thermostat settings were also adjusted and set correctly.The AC unit was then restarted and monitored.Cooling performance was observed to be normal, and the unit is currently operating properly with normal cooling. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
493 | Sirti-WAN-R3-Ticket-463 | NA | 2026-06-22 | P008C3-ENC01-UPE-01 | Aaqib | CPU temperature too High | High Temperature | A/C condenser Fan and comperessor are faulty |  | Zone 55 | 25.2614822° 51.4801647° | Outside Doha | P3 - Medium | 2026-06-22 08:44 | 2026-06-22 08:46 | 2.2333 | 2026-06-22 08:44 | 2026-06-22 17:11 | 507.6833 | 507.6833 | A site visit was conducted to inspect the AC unit and power cables. During the inspection, the AC unit was removed, and a faulty condenser fan was identified and replaced with a new one. Following the replacement, the AC unit operated normally and provided effective cooling. However, after approximately 30 minutes of operation, the compressor shut down, confirming that the compressor is faulty and requires replacement | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
494 | Sirti-WAN-R3-Ticket-464 | NA | 2026-06-22 | DUK-ENC12-UPE-02 | Aaqib | CPU temperature too High | High Temperature | A/C1 breaker tripped and the A/C2 compressor is faulty |  | Zone 72 | 25.4302156° 51.1497491° | Outside Doha | P3 - Medium | 2026-06-22 13:47 | 2026-06-22 13:52 | 4.4333 | 2026-06-22 16:11 | 2026-06-22 16:12 | 1.9333 | 145.4 | The faulty compressor was disconnected, and the A/C1 compressor was connected and placed in operation for A/C2. Currently, only one A/C unit is functioning normally, while the other unit operates in fan mode only due to the disconnected compressor. Both A/C units were cleaned using a blower and cloth towels, and the operating AC was observed to be cooling effectively and performing well. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
495 | Sirti-WAN-R3-Ticket-465 | NA | 2026-06-22 | P010-ENC89-UPE-02 | Abubaker | CPU temperature too High | High Temperature | Auto cleared before FLM reach the site |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | P3 - Medium | 2026-06-22 15:24 | 2026-06-22 15:34 | 9.85 | 2026-06-22 15:24 | 2026-06-22 15:44 | 19.6333 | 19.6333 | The condenser and filters were found blocked and were cleaned using a chemical wash. The refrigerant gas level was checked, and high pressure was observed; therefore, the gas charge was adjusted accordingly. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Rizwan
496 | Sirti-WAN-R3-Ticket-466 | NA | 2026-06-23 | P004-TMC-NPE-01 | Adel | Power Module stopped working | power alarm | Tunnel team is doing activity on site |  | Zone 51 | 25.319385 51.352255 | Outside Doha | P3 - Medium | 2026-06-23 08:02 | 2026-06-23 08:03 | 1 | 2026-06-23 08:02 | 2026-06-23 08:06 | 3.8167 | 3.8167 | Tunnel team is doing activity on site | Completed | Non-maintainer | 3rd Party | N/a | Alarm Cleared | -
497 | Sirti-WAN-R3-Ticket-467 | NA | 2026-06-23 | P002-ENC34-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-06-23 11:26 | 2026-06-23 11:28 | 2 | 2026-06-23 11:26 | 2026-06-23 11:31 | 5.35 | 5.35 | kahromaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
498 | Sirti-WAN-R3-Ticket-468 | NA | 2026-06-23 | P004-ENC43-UPE-02 | Adel | Temperature higher than Upper threshold | High Temperature | A/C was not cooling properly |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-06-23 14:26 | 2026-06-23 14:29 | 3 | 2026-06-23 14:26 | 2026-06-23 14:34 | 7.65 | 7.65 | Alarm cleared before the FLM team reached the site; however, the team proceeded with the site visit and inspected the AC unit. All electrical parameters were found to be within normal operating limits. The air filters were cleaned due to blockage, and the thermostat settings were adjusted as required. The unit was then restarted and tested. Cooling performance was verified to be normal, and the AC is now operating properly. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Rizwan
499 | Sirti-WAN-R3-Ticket-469 | NA | 2026-06-23 | P004-ENC43-CE-01 P004-ENC43-UPE-02 P023C2-ENC43-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power inturruption |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P2 - High | 2026-06-23 20:44 | 2026-06-23 20:45 | 1.1333 | 2026-06-23 20:44 | 2026-06-23 20:50 | 6.1167 | 6.1167 | kahromaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
500 | Sirti-WAN-R3-Ticket-470 | NA | 2026-06-24 | P002-ENC34-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-06-24 09:32 | 2026-06-24 09:34 | 2 | 2026-06-24 09:32 | 2026-06-24 09:37 | 4.4833 | 4.4833 | kahromaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
501 | Sirti-WAN-R3-Ticket-471 | NA | 2026-06-24 | DUK-ENC24-CE-01 | Adel | CRC error alarm | CRC error alarm | CAT6 cable is damaged |  | Zone 85 | 25.435778° 51.0066732° | Outside Doha | P4 - Low | 2026-06-24 06:09 | 2026-06-24 06:12 | 3 | 2026-06-24 09:30 | 2026-06-24 09:40 | 10 | 211.1167 | FLM replaced damaged CAT6 cable | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Hicham
502 | Sirti-WAN-R3-Ticket-472 | NA | 2026-06-24 | P007C5P1-ENC31-CE-01 | Adel | Link Down | LAN link down | LAN device was not responding due to high temperature |  | Zone 52 | 25.306727 51.411587 | Outside Doha | P3 - Medium | 2026-06-24 10:56 | 2026-06-24 10:59 | 3 | 2026-06-24 15:32 | 2026-06-24 15:43 | 11.25 | 287.0167 | FLM Team restarted the LAN switch and alarm cleared once the switch rebooted | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Khadar
503 | Sirti-WAN-R3-Ticket-473 | NA | 2026-06-24 | P008C2-ENC33-CE-01 | Adel | Link Down | LAN link down | LAN switch was not responding due to high temperature |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P3 - Medium | 2026-06-24 14:14 | 2026-06-24 14:17 | 3 | 2026-06-24 15:38 | 2026-06-24 15:49 | 11.3333 | 95.2167 | FLM Team restarted SCADA switch and alarm cleared once the switch rebooted | Completed | Non-maintainer | node Up | N/a | Alarm Cleared | Irshad
504 | Sirti-WAN-R3-Ticket-474 | NA | 2026-06-24 | P008C2-ENC33-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | CB Tripped during A/C troubleshooting |  | Zone 44 | 25.2377365° 51.5294852° | Outside Doha | P2 - High | 2026-06-24 20:11 | 2026-06-24 20:15 | 3.9167 | 2026-06-24 20:11 | 2026-06-24 20:17 | 5.9333 | 5.9333 | FLM was on site for A/C troubleshooting and device CB tripped, FLM switch on the tripped CB and device restored | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Khadar
505 | Sirti-WAN-R3-Ticket-475 | NA | 2026-06-25 | P014-Enc10-DSW10 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Intermittent Disconnection |  | Zone 45 | 25.253896 51.535995 | Outside Doha | P2 - High | 2026-06-25 00:12 | 2026-06-25 00:12 | 0.15 | 2026-06-25 00:12 | 2026-06-25 00:12 | 0.15 | 0.15 | Intermittent Disconnection observed but clear automatically. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
506 | Sirti-WAN-R3-Ticket-476 | NA | 2026-06-25 | P014-Enc12-DSW12 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Intermittent Disconnection |  | Zone 45 | 25.524911 51.54895 | Outside Doha | P2 - High | 2026-06-25 00:12 | 2026-06-25 00:14 | 1.5167 | 2026-06-25 00:12 | 2026-06-25 00:14 | 1.6667 | 1.5167 | Intermittent Disconnection observed but clear automatically. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
507 | Sirti-WAN-R3-Ticket-477 | NA | 2026-06-25 | P060-TCR-NPE-01 P060-TCR-USG-01 P060-TCR-USG-02 | Adel | module power stopped working | power alarm | P060 control room tem are performing power activity |  | Zone 70 | 25.545418° 51.446774° | Outside Doha | P3 - Medium | 2026-06-25 08:31 | 2026-06-25 08:33 | 2 | 2026-06-25 08:31 | 2026-06-25 08:51 | 19.6 | 19.6 | P060 control room tem are performing power activity | Completed | Non-maintainer | 3rd Party | N/a | Alarm Cleared | -
508 | Sirti-WAN-R3-Ticket-478 | NA | 2026-06-25 | P012-ENC33-CE-01.omc.local | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | CB Tripped during A/C PPM Activity |  | Zone 56 | 25.2282194° 51.5019836° | Outside Doha | P2 - High | 2026-06-25 18:16 | 2026-06-25 18:20 | 4.0667 | 2026-06-25 18:16 | 2026-06-25 18:22 | 6.2833 | 6.2833 | FLM was on site for A/C PPM and device CB tripped, FLM switch on the tripped CB and device restored | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Khadar
509 | Sirti-WAN-R3-Ticket-479 | NA | 2026-06-26 | P001-ENC11A-CE01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power inturruption |  | Zone 91 | 25.22294 51.54811 | Outside Doha | P2 - High | 2026-06-26 11:27 | 2026-06-26 11:29 | 2 | 2026-06-26 11:27 | 2026-06-26 11:32 | 5.1 | 5.1 | kahromaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
510 | Sirti-WAN-R3-Ticket-480 | NA | 2026-06-27 | P011-ENC58-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 49 | 25.2273162° 51.5921766° | Outside Doha | P2 - High | 2026-06-27 01:22 | 2026-06-27 01:25 | 3.2167 | 2026-06-27 01:54 | 2026-06-27 01:55 | 1.05 | 33.2833 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | Rizwan
511 | Sirti-WAN-R3-Ticket-481 | NA | 2026-06-27 | Sal-Enc56-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 96 | 24.8911735° 50.938318° | Outside Doha | P2 - High | 2026-06-27 07:52 | 2026-06-27 07:53 | 1.0167 | 2026-06-27 07:52 | 2026-06-27 07:55 | 2.1167 | 2.1167 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
512 | Sirti-WAN-R3-Ticket-482 | NA | 2026-06-27 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-06-27 09:48 | 2026-06-27 09:52 | 4.2333 | 2026-06-27 09:48 | 2026-06-27 09:52 | 4.4833 | 4.4833 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
513 | Sirti-WAN-R3-Ticket-483 | NA | 2026-06-27 | P059C1-N3-ENC33-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 70 | 25.53313695° 51.41207372° | Outside Doha | P2 - High | 2026-06-27 19:32 | 2026-06-27 19:35 | 3 | 2026-06-27 19:32 | 2026-06-27 19:37 | 5.9167 | 5.9167 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
514 | Sirti-WAN-R3-Ticket-484 | NA | 2026-06-27 | SAL-ENC14-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 55 | 25.1858801° 51.3628538° | Outside Doha | P2 - High | 2026-06-27 21:27 | 2026-06-27 21:29 | 2 | 2026-06-27 21:27 | 2026-06-27 21:29 | 2.6667 | 2.6667 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
515 | Sirti-WAN-R3-Ticket-485 | NA | 2026-06-27 | SAL-ENC14-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 55 | 25.1858801° 51.3628538° | Outside Doha | P2 - High | 2026-06-27 23:22 | 2026-06-27 23:23 | 1.3333 | 2026-06-27 23:23 | 2026-06-27 23:24 | 1.0667 | 2.6833 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
516 | Sirti-WAN-R3-Ticket-486 | NA | 2026-06-28 | SAL-ENC14-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 55 | 25.1858801° 51.3628538° | Outside Doha | P2 - High | 2026-06-28 00:21 | 2026-06-28 00:23 | 2.1167 | 2026-06-28 01:57 | 2026-06-28 01:58 | 1.05 | 97.3333 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | Sarjoon
517 | Sirti-WAN-R3-Ticket-487 | NA | 2026-06-28 | P005-TCR-CE-01 P005-TCR-CE-02 | Sanket | Link Down | LAN link down | P005-TCR-CE-01 and P005-TCR-CE-02 Port Te 1/0/12 towards SUB-ST-74-ACSW01 |  | Zone 51 | 25.3199307° 51.447548° | Outside Doha | P3 - Medium | 2026-06-28 00:16 | 2026-06-28 00:27 | 11 | 2026-06-28 00:29 | 2026-06-28 00:30 | 1.1833 | 14.25 | The GBDG team is carrying out work on the fiber core connected to the radio, which has caused the link to go down. | Completed | Non-maintainer | 3rd Party | GBDG | Alarm Cleared | -
518 | Sirti-WAN-R3-Ticket-488 | NA | 2026-06-28 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-06-28 09:45 | 2026-06-28 09:48 | 2.3667 | 2026-06-28 09:45 | 2026-06-28 09:50 | 5.0167 | 5.0167 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
519 | Sirti-WAN-R3-Ticket-489 | NA | 2026-06-28 | RAA-ENC24-UPE-02 RAA-ENC24-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power inside WAN cabinet and AC CB tripped due to AC short circuit |  | Zone 49 | 25.23647° 51.58650° | Outside Doha | P2 - High | 2026-06-28 20:02 | 2026-06-28 20:04 | 2 | 2026-06-28 20:33 | 2026-06-28 20:55 | 21.3167 | 52.3167 | FLM switched on tripped CB at WAN cabinet and after troubleshooting the AC ,team replaced faulty compressor relay of the AC | Completed | Non-maintainer | Defect | AC | Device Restored | Rizwan
520 | Sirti-WAN-R3-Ticket-490 | NA | 2026-06-29 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-06-29 09:32 | 2026-06-29 09:34 | 2.25 | 2026-06-29 09:32 | 2026-06-29 09:36 | 4.15 | 4.15 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
521 | Sirti-WAN-R3-Ticket-491 | NA | 2026-06-30 | DUK-ENC24-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Device went down during Planned Sheduled PPM |  | Zone 85 | 25.435778° 51.0066732° | Outside Doha | P2 - High | 2026-06-30 06:42 | 2026-06-30 06:44 | 2.3333 | 2026-06-30 06:47 | 2026-06-30 06:48 | 1 | 6.3333 | Device went down during Planned Sheduled PPM | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Ghulam
522 | Sirti-WAN-R3-Ticket-492 | NA | 2026-06-30 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-06-30 09:26 | 2026-06-30 09:28 | 2.2 | 2026-06-30 09:26 | 2026-06-30 09:31 | 5.35 | 5.35 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
523 | Sirti-WAN-R3-Ticket-493 | 27078111 | 2026-06-30 | P011-Enc55-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | no output power from UPS | DA49-PRM2000-ITS-ENC-00004 | Zone 49 | 25.2209722° 51.5862222° | Outside Doha | P2 - High | 2026-06-30 13:35 | 2026-06-30 13:40 | 5.3167 | 2026-06-30 15:28 | 2026-06-30 15:46 | 17.25 | 130.8167 | FLM pypassed the Faulty UPS and connected devices directly to kahromaa | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Khadar
524 | Sirti-WAN-R3-Ticket-494 | NA | 2026-06-30 | P007C5P1-ENC26-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 55 | 25.2663028° 51.4683846° | Outside Doha | P2 - High | 2026-06-30 16:00 | 2026-06-30 16:02 | 2 | 2026-06-30 16:00 | 2026-06-30 16:11 | 10.8333 | 10.8333 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
525 | Sirti-WAN-R3-Ticket-495 | NA | 2026-07-01 | P007C7P2-ENC15-CE-01 P007C7P2-ENC15-UPE-01 P007C7P2-ENC048-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Device went down during Planned Scheduled PPM |  | Zone 51 | 25.232063° 51.45943° | Outside Doha | P2 - High | 2026-07-01 01:20 | 2026-07-01 01:21 | 1 | 2026-07-01 01:25 | 2026-07-01 01:26 | 1.0667 | 6.0833 | Device went down during Planned Sheduled PPM | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Rizwan
526 | Sirti-WAN-R3-Ticket-496 | NA | 2026-07-01 | P007C7P2-ENC15-CE-01 P007C7P2-ENC15-UPE-01 P007C7P2-ENC048-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Device went down during Planned Scheduled PPM |  | Zone 51 | 25.232063° 51.45943° | Outside Doha | P2 - High | 2026-07-01 01:39 | 2026-07-01 01:41 | 2.0667 | 2026-07-01 01:43 | 2026-07-01 01:44 | 1.1 | 5.45 | Device went down during Planned Sheduled PPM | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Rizwan
527 | Sirti-WAN-R3-Ticket-497 | NA | 2026-07-01 | P007C7P2-ENC15-CE-01 P007C7P2-ENC15-UPE-01 P007C7P2-ENC048-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned PPM activity with temporary power shutdown to bypass the RCCB and carry out further testing. |  | Zone 51 | 25.232063° 51.45943° | Outside Doha | P2 - High | 2026-07-01 02:34 | 2026-07-01 02:36 | 2 | 2026-07-01 03:06 | 2026-07-01 03:07 | 1 | 32.7833 | Planned PPM activity with temporary power shutdown to bypass the RCCB and carry out further testing. | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Rizwan
528 | Sirti-WAN-R3-Ticket-498 | NA | 2026-07-01 | P007C5P1-ENC26-CE-01.omc.local | Aaqib | Link Down | Port Gi 1/24 Down towards LAN | Port Gi 1/24 (P007C5-USW-26-2) Down towards LAN |  | Zone 55 | 25.2663028° 51.4683846° | Outside Doha | P3 - Medium | 2026-07-01 10:04 | 2026-07-01 10:09 | 5 | 2026-07-01 15:40 | 2026-07-01 15:56 | 16.2833 | 352.6833 | Switch was faulty and replaced by LAN team. | Completed | Non-maintainer | Environmental | Heat summer | Device Restored
529 | Sirti-WAN-R3-Ticket-499 | NA | 2026-07-01 | P059C1-N3-ENC33-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 70 | 25.53313695° 51.41207372° | Outside Doha | P2 - High | 2026-07-01 10:14 | 2026-07-01 10:17 | 3 | 2026-07-01 10:04 | 2026-07-01 10:28 | 24.4333 | 14.1 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
530 | Sirti-WAN-R3-Ticket-500 | NA | 2026-07-01 | RAA-ENC01-CE-01 | Aaqib | Link Down | Port XGE 0/0/3 Down towards LAN | Port XGE 0/0/3 (ENC-01-USW-03) Down towards LAN |  | Zone 27 | 25.28386° 51.55571° | Inside Doha | P3 - Medium | 2026-07-01 11:14 | 2026-07-01 11:19 | 4.8 | 2026-07-01 15:40 | 2026-07-01 16:00 | 20.05 | 286 | LAN SW hanged due to high temperature after rebooting port become Up | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
531 | Sirti-WAN-R3-Ticket-501 | NA | 2026-07-01 | RAA-ENC01-UPE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC Compressor faulty |  | Zone 27 | 25.28386° 51.55571° | Inside Doha | P3 - Medium | 2026-07-01 11:17 | 2026-07-01 11:20 | 3.3833 | 2026-07-01 11:17 | 2026-07-01 11:33 | 15.75 | 15.75 | AC is fault , team is still searching the AC spare parts | Completed | Non-maintainer | Defect | AC | Device Restored
532 | Sirti-WAN-R3-Ticket-502 | NA | 2026-07-01 | COR-ENC12-CE-01 | Adel | Link Down | Port XGE 0/0/4 Down towards LAN | LAN Team is replacing LAN switch |  | Zone 61 | 25.324005699251956 51.52792742883553 | Inside Doha | P3 - Medium | 2026-07-01 18:31 | 2026-07-01 18:33 | 2 | 2026-07-01 18:31 | 2026-07-01 18:51 | 19.5 | 19.5 | LAN Team is replacing LAN switch | Completed | Non-maintainer | Planned Activity | Planned Activity | Alarm Cleared
533 | Sirti-WAN-R3-Ticket-503 | NA | 2026-07-01 | SAl-ENC26-CE-01 | Aaqib | Link Down | 25GE 1/0/2 Connected to LSW-04 25GE 1/0/3 Connected to LSW-03 | Planned Kahrama outage at LAN side |  | Zone 81 | 25.1435454° 51.2478413° | Outside Doha | P3 - Medium | 2026-07-01 06:46 | 2026-07-01 06:50 | 4.2167 | 2026-07-01 07:33 | 2026-07-01 10:49 | 195.6833 | 242.7833 | Planned Kahrama outage at LAN side | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared
534 | Sirti-WAN-R3-Ticket-504 | NA | 2026-07-02 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-07-02 09:17 | 2026-07-02 09:20 | 2.9333 | 2026-07-02 09:17 | 2026-07-02 09:22 | 4.5 | 4.5 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
535 | Sirti-WAN-R3-Ticket-505 | NA | 2026-07-02 | DC23-ENC101-CE-01 | Adel | optical model temprature too high | High Temperature | AC Compressor faulty |  | Zone 51 | 25.3204° 51.470367° | Outside Doha | P3 - Medium | 2026-07-02 15:27 | 2026-07-02 15:30 | 3 | 2026-07-02 16:42 | 2026-07-02 16:48 | 6.15 | 81.3667 | Upon inspection, the power supply and voltage were verified, and all AC unit components were checked. It was found that the compressor terminal power cable had been burned and was replaced with a new one. The 35 µF capacitor was also replaced. The unit was thoroughly cleaned using a blower and cloth towels to remove dust and debris. After completing the repairs and maintenance, the AC unit was tested and confirmed to be operating normally, with proper cooling performance and satisfactory overall operation. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
536 | Sirti-WAN-R3-Ticket-506 | NA | 2026-07-03 | SAL-ENC32-CE-01 | Abubaker | Link Down | LAN link down | Alarm Auto Cleared before FLM reached the site |  | Zone 82 | 25.1165799° 51.1812367° | Outside Doha | P3 - Medium | 2026-07-03 01:48 | 2026-07-03 01:52 | 4.4333 | 2026-07-03 01:48 | 2026-07-03 02:18 | 30.0333 | 30.0333 | The link is down towards local device and Autorestored. | Completed | Non-maintainer | 3rd Party | RF001 | Alarm Cleared | -
537 | Sirti-WAN-R3-Ticket-507 | NA | 2026-07-03 | P017C2-ENC23-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | CB is tripped due to planned PPM |  | Zone 57 | 25.1702778° 51.4710278° | Outside Doha | P2 - High | 2026-07-03 19:13 | 2026-07-03 19:15 | 2 | 2026-07-03 19:13 | 2026-07-03 19:20 | 6.95 | 6.95 | CB is tripped due to planned PPM | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Khadar
538 | Sirti-WAN-R3-Ticket-508 | NA | 2026-07-04 | 22FEB-ENC15-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 54 | 25.28160814° 51.48539846° | Outside Doha | P2 - High | 2026-07-04 06:37 | 2026-07-04 06:41 | 4.2667 | 2026-07-04 06:37 | 2026-07-04 06:54 | 17.1167 | 17.1167 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
539 | Sirti-WAN-R3-Ticket-509 | NA | 2026-07-05 | SAL-ENC50-CE-01 | Aaqib | Link Down | LAN link down | Port 25GE 1/0/4 connected to (ENC50-SAL-LAN-Ring) down due to Planned khaharama Activity at LAN side |  | Zone 96 | 24.9513076° 50.9993542° | Outside Doha | P3 - Medium | 2026-07-05 07:20 | 2026-07-05 07:24 | 3.8333 | 2026-07-05 09:04 | 2026-07-05 09:44 | 40.1 | 144.5833 | Planned Kahrama outage at LAN side | Completed | Non-maintainer | Planned Activity | State Kahramaa | Alarm Cleared
540 | Sirti-WAN-R3-Ticket-510 | NA | 2026-07-05 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-07-05 09:37 | 2026-07-05 09:39 | 2.1167 | 2026-07-05 09:37 | 2026-07-05 09:42 | 4.6667 | 4.6667 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
541 | Sirti-WAN-R3-Ticket-511 | NA | 2026-07-05 | 22FEB-ENC25-UPE-02 | Aaqib | CPU temperature too High | High Temperature | Relay is Faulty |  | Zone 51 | 25.31832397° 51.47088144° | Outside Doha | P3 - Medium | 2026-07-05 13:44 | 2026-07-05 13:47 | 3.1 | 2026-07-05 15:31 | 2026-07-05 16:02 | 31 | 137.8333 | After opening the AC unit for inspection, we identified that the compressor OLP relay was faulty. The defective OLP relay was replaced with a new one, after which the AC breaker was switched back on. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khader
542 | Sirti-WAN-R3-Ticket-512 | NA | 2026-07-05 | P006-ENC17-UPE-02 | Aaqib | CPU temperature too High | High Temperature | Temperature Parameters setting issue |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P3 - Medium | 2026-07-05 13:59 | 2026-07-05 14:04 | 4.2667 | 2026-07-05 15:33 | 2026-07-05 16:08 | 34.95 | 128.2167 | Temperature get normalized after adjsuting Parameters in Temperatrue controller | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Patrick
543 | Sirti-WAN-R3-Ticket-513 | NA | 2026-07-05 | P010-ENC01-UPE-01 | Aaqib | CPU temperature too High | High Temperature | Temperature autorestore |  | Zone 81 | 25.1398815° 51.4073931° | Outside Doha | P3 - Medium | 2026-07-05 14:24 | 2026-07-05 14:28 | 3.7833 | 2026-07-05 14:40 | 2026-07-05 14:41 | 1 | 16.8333 | The Temperature issue auto restore | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
544 | Sirti-WAN-R3-Ticket-514 | 27142512 | 2026-07-05 | P006-ENC17-UPE-02 P006-ENC17-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | UPS Output issue | RA56-PRM0100-ITS-ITW-00008 | Zone 56 | 25.19542° 51.454° | Outside Doha | P2 - High | 2026-07-05 14:58 | 2026-07-05 15:03 | 4.1833 | 2026-07-05 15:33 | 2026-07-05 16:08 | 34.95 | 69.1333 | The UPS output issue has been identified, and the team has implemented a bypass to maintain operations. | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Patrick
545 | Sirti-WAN-R3-Ticket-515 | NA | 2026-07-05 | P002-ENC07-UPE-01 | Sanket | Card Stopped working | Card Stopped working | Card auto rebooted due to high temperature |  | Zone 55 | 25.257° 51.486° | Outside Doha | P3 - Medium | 2026-07-05 16:20 | 2026-07-05 16:21 | 1 | 2026-07-05 16:21 | 2026-07-05 16:22 | 0.95 | 2.1167 | Card take hard reboot due to high temperature | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
546 | Sirti-WAN-R3-Ticket-516 | NA | 2026-07-06 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-07-06 09:04 | 2026-07-06 09:07 | 2.1 | 2026-07-06 09:04 | 2026-07-06 09:09 | 4.4667 | 4.4667 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
547 | Sirti-WAN-R3-Ticket-517 | 27153849 | 2026-07-06 | 22FEB-ENC13-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | ATS breaker was tripped OFF in ITS-FP-10 | DA39-PRM0251-ITS-ITW-00001 | Zone 55 | 25.27506948° 51.48993629° | Outside Doha | P2 - High | 2026-07-06 10:07 | 2026-07-06 10:10 | 3.1833 | 2026-07-06 15:30 | 2026-07-06 15:42 | 11.9167 | 334.6333 | ATS breaker was tripped OFF in ITS-FP-10 | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Najeeb
548 | Sirti-WAN-R3-Ticket-518 | NA | 2026-07-06 | P006-ENC17-UPE-02 | Aaqib | CPU temperature too High | High Temperature | Compressor, capacitor, capillary pipe, and dry filter found faulty |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P3 - Medium | 2026-07-06 08:04 | 2026-07-06 08:09 | 4.4 | 2026-07-06 08:36 | 2026-07-06 08:44 | 7.3833 | 39.5 | Compressor, capacitor, capillary pipe, and dry filter replaced and Gas refilled | Completed | Non-maintainer | Defect | AC Defect | Alarm Cleared | -
549 | Sirti-WAN-R3-Ticket-519 | NA | 2026-07-06 | P007C5P1-ENC30-CE-01.omc.local | Sanket | Link Down | LAN link down | Device Abnormal. Issue handed over to LAN |  | Zone 55 | 25.30204, 51.42094 | Outside Doha | P3 - Medium | 2026-07-06 19:03 | 2026-07-06 19:10 | 7.2667 | 2026-07-06 19:31 | 2026-07-06 20:31 | 60 | 87.75 | The LAN device is malfunctioning | Completed | Non-maintainer | Defect | Handed Over | -
550 | Sirti-WAN-R3-Ticket-520 | NA | 2026-07-07 | SAL-ENC09-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Power interruption due to Contractor (Polaris) activity |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-07-07 03:21 | 2026-07-07 03:23 | 2 | 2026-07-07 03:21 | 2026-07-07 03:30 | 8.9833 | 8.9833 | Power interrupted due to contractor activity on street light feeder pillar, Device restored before FLM team reach the site | Completed | Non-maintainer | 3rd Party | Polaris | Device Restored | -
551 | Sirti-WAN-R3-Ticket-521 | NA | 2026-07-07 | 22FEB-ENC25-CE-01 | Aaqib | Link Down | LAN link down | kahramaa power inturruption towards LAN |  | Zone 51 | 25.31832397° 51.47088144° | Outside Doha | P3 - Medium | 2026-07-07 07:49 | 2026-07-07 07:54 | 4.4 | 2026-07-07 07:49 | 2026-07-07 07:59 | 9.2333 | 9.2333 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared
552 | Sirti-WAN-R3-Ticket-522 | NA | 2026-07-07 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-07-07 10:07 | 2026-07-07 10:10 | 3.0833 | 2026-07-07 10:07 | 2026-07-07 10:12 | 4.65 | 4.65 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
553 | Sirti-WAN-R3-Ticket-523 | NA | 2026-07-07 | P006-ENC17-UPE-02 | Aaqib | CPU temperature too High | High Temperature | high temperature inside the cabinet due to a blockage in the AC evaporator and condenser, which was restricting refrigerant flow and reducing the cooling performance. |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P3 - Medium | 2026-07-07 10:07 | 2026-07-07 10:16 | 8.7 | 2026-07-07 15:31 | 2026-07-07 15:53 | 22.7 | 346.6 | The AC unit was opened and the evaporator and condenser were cleaned using 141B flushing chemical. The refrigeration circuit was flushed with 141B and nitrogen gas, and the dry filter and capillary tube were replaced. The AC unit was then reassembled, installed back into the cabinet, and tested. The unit is now operating normally, providing proper cooling, and the cabinet temperature has returned to the normal range. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khader
554 | Sirti-WAN-R3-Ticket-524 | NA | 2026-07-07 | P023C3-ENC174-CE-01 P023C3-ENC21-CE-01 | Sanket | VRRP Switchover | VRRP Switchover | VRRP switching and CRC errors were observed on P023C3-ENC174-CE-01 interface XGE 0/0/1 |  | Zone 94 | 25.0168866° 51.490473° | Outside Doha | P3 - Medium | 2026-07-07 21:40 | 2026-07-07 21:48 | 8 | 2026-07-07 23:00 | 2026-07-07 23:23 | 22.4667 | 102.5667 | Existing Patch Cord replaced with a new one | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Rizwan
555 | Sirti-WAN-R3-Ticket-525 | NA | 2026-07-08 | P028C2-ENC-01-CE-01.omc.local P028C2-ENC14-CE-01.omc.local | Abubaker | Link Down | WAN Link Down | P028C2-ENC-01-CE-01.omc.local Port Te1/25 toward P028C2-ENC14-CE-01.omc.local Port Te1/26 is down - No optical Rx power |  | Zone 03 | 25.2839108° 51.5496128° 25.2825567° 51.524715° | Outside Doha | P3 - Medium | 2026-07-08 04:18 | 2026-07-08 04:27 | 9.5 | 2026-07-08 05:39 | 2026-07-08 05:51 | 12.0833 | 93.4167 | Cleaned the SFP for the interface Te1/26 at P028C2-ENC14-CE-01.omc.local and restarted the port | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Hicham
556 | Sirti-WAN-R3-Ticket-526 | NA | 2026-07-08 | P007C2-Enc59-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | UPS input breaker was tripped |  | Zone 54 | 25.2922123° 51.4648447° | Outside Doha | P2 - High | 2026-07-08 08:34 | 2026-07-08 08:37 | 2.4333 | 2026-07-08 09:11 | 2026-07-08 09:13 | 2.4167 | 39.0833 | UPS input breaker was tripped | Completed | Non-maintainer | UPS Defect | UPS | Alarm Cleared | Hicham
557 | Sirti-WAN-R3-Ticket-527 | NA | 2026-07-08 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-07-08 09:27 | 2026-07-08 09:28 | 1.15 | 2026-07-08 09:27 | 2026-07-08 09:38 | 11.5 | 11.5 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | -
558 | Sirti-WAN-R3-Ticket-528 | NA | 2026-07-08 | P006-ENC17-UPE-02 | Aaqib | CPU temperature too High | High Temperature | Temperature Parameters setting issue |  | Zone 56 | 25.19542° 51.454° | Outside Doha | P3 - Medium | 2026-07-08 14:36 | 2026-07-08 14:38 | 2.3 | 2026-07-08 15:30 | 2026-07-08 15:44 | 14.4 | 68.5667 | Restart the AC and set the temperature | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khader
559 | Sirti-WAN-R3-Ticket-529 | NA | 2026-07-09 | P028C2-ENC-01-CE-01.omc.local P028C2-ENC14-CE-01.omc.local | Abubaker | Link Down | WAN Link Down | P028C2-ENC-01-CE-01.omc.local Port Te1/25 toward P028C2-ENC14-CE-01.omc.local Port Te1/26 is down - optical Rx power very low |  | Zone 17 | 25.2839108° 51.5496128° 25.2825567° 51.524715° | Outside Doha | P3 - Medium | 2026-07-09 00:08 | 2026-07-09 00:10 | 1.6 | 2026-07-09 00:49 | 2026-07-09 01:14 | 25.15 | 65.7833 | Existing Patch Cord for Te1/25 at P028C2-ENC-01-CE-01.omc.local replaced with a new one | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Hassan
560 | Sirti-WAN-R3-Ticket-530 | 27198468 | 2026-07-09 | CRR-ENC37-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | UPS Malfunctioning |  | Zone 40 | 25.265846° 51.500562° | Inside Doha | P2 - High | 2026-07-09 02:41 | 2026-07-09 02:44 | 2.8667 | 2026-07-09 04:15 | 2026-07-09 04:49 | 34.25 | 127.75 | FLM team connected the Generator as the UPS is not functioning | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Umair
561 | Sirti-WAN-R3-Ticket-531 | NA | 2026-07-09 | CRR-ENC37-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Generator was connected |  | Zone 40 | 25.265846° 51.500562° | Inside Doha | P2 - High | 2026-07-09 05:34 | 2026-07-09 05:34 | 0 | 2026-07-09 05:34 | 2026-07-09 05:42 | 8.1167 | 8.1167 | Disconnected the power generator and connected back the UPS | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Ghulam
562 | Sirti-WAN-R3-Ticket-532 | NA | 2026-07-09 | P002-ENC34-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Power cable tracing |  | Zone 56 | 25.2292791° 51.4377406° | Outside Doha | P2 - High | 2026-07-09 07:16 | 2026-07-09 07:17 | 1.1 | 2026-07-09 07:17 | 2026-07-09 07:17 | 0 | 1.1 | Planned activity for UPS to Switch Power cable tracing and bypassing UPS | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Ghulam
563 | Sirti-WAN-R3-Ticket-533 | NA | 2026-07-09 | Duk-Enc06-CE-01 | Aaqib | Link Down | LAN link down | Port GE 1/0/9 (Local Nodes) is down |  | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | P3 - Medium | 2026-07-09 09:46 | 2026-07-09 09:49 | 3.4833 | 2026-07-09 16:10 | 2026-07-09 16:19 | 9 | 393.1 | FLM replaced Ethernet cable connected to POE to CCTV , alarm is still flapping , issue is related to RMC | Completed | Non-maintainer | 3rd Party | RMC | Alarm Cleared | Khader
564 | Sirti-WAN-R3-Ticket-534 | NA | 2026-07-09 | P006-ENC17-UPE02 | Adel | CPU temperature too High | High Temperature | High Temperature |  | Zone 56 | 25.19614, 51.45325 | Outside Doha | P3 - Medium | 2026-07-09 16:01 | 2026-07-09 16:04 | 3 | 2026-07-09 17:06 | 2026-07-09 17:08 | 3 | 67.6667 | FLM cleaned the AC and checked functionality | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
565 | Sirti-WAN-R3-Ticket-535 | NA | 2026-07-09 | P059C1-ENC04-CE-01 | Adel | Link Down | LAN link down | P059C1-ENC04-CE-01 _Port XGE 0/0/1 towards LAN BSW ENC04 |  | Zone 71 | 25.3653937° 51.4467471° | Outside Doha | P3 - Medium | 2026-07-09 20:50 | 2026-07-09 20:52 | 2 | 2026-07-09 20:50 | 2026-07-09 21:08 | 17.5333 | 17.5333 | LAN team is doing Migration of LAN switches | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | hassan
566 | Sirti-WAN-R3-Ticket-536 | NA | 2026-07-09 | P059C1-ENC42-CE-01 | Adel | Link Down | LAN link down | P059C1-ENC42-CE-01_Port XGE 0/0/2 |  | Zone 70 | 25.56931971° 51.41540451° | Outside Doha | P3 - Medium | 2026-07-09 21:01 | 2026-07-09 21:02 | 1 | 2026-07-09 21:01 | 2026-07-09 22:03 | 62.6667 | 62.6667 | LAN team is doing Migration of LAN switches | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | Najeeb
567 | Sirti-WAN-R3-Ticket-537 | NA | 2026-07-09 | P059C1-ENC20-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | planned activity of LAN Team |  | Zone 70 | 25.44194931° 51.41112813° | Outside Doha | P2 - High | 2026-07-09 22:07 | 2026-07-09 22:11 | 4 | 2026-07-09 22:07 | 2026-07-09 22:23 | 16.4167 | 16.4167 | while LAN team was installing new switched inside the cabinet , CB was tripped , team switched on the CB | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Najeeb
568 | Sirti-WAN-R3-Ticket-538 | NA | 2026-07-10 | P007C7P1-ENC10-CE-01 P007C7P1-ENC06-CE-01 P007C7P1-ENC04-CE-01 P007C7P1-ENC03-CE-01 P007C7P1-ENC01-CE-01 P007C7P1-ENC05-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Management Flapping | Management of 6 devices is flapping at P007C7P1 schema related to Al Salam Tech |  | Zone 30 | 25.344747° 51.457503° | Inside Doha | P2 - High | 2026-07-10 00:24 | 2026-07-10 00:30 | 5.7 | 2026-07-10 00:24 | 2026-07-10 16:01 | 936.2833 | 936.2833 | The issue was escalated to Al Salam Tech, and the required access to ENC10 was obtained. The faulty device was identified, isolated, and eliminated, which restored schema management and cleared all alarms. For the management of the WAN device, the broadcast from LAN switch EX77964 (LAN) was identified, isolated, and eliminated, which restored schema management | Completed | Non-maintainer | 3rd Party | Salam Tech | Alarm Cleared | Ahmed Amir
569 | Sirti-WAN-R3-Ticket-539 | NA | 2026-07-10 | P059C1-ENC20-CE-01 | Abubaker | Link Down | LAN link down | P059C1-ENC04-CE-01 _Port XGE 0/0/1 towards LAN ENC42 is disconnected |  | Zone 70 | 25.44194931° 51.41112813° | Outside Doha | P3 - Medium | 2026-07-10 01:00 | 2026-07-10 01:10 | 10.25 | 2026-07-10 01:00 | 2026-07-10 04:05 | 185.25 | 185.25 | Port is shutdown and to be enabled during the LAN migration activity | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | -
570 | Sirti-WAN-R3-Ticket-540 | NA | 2026-07-10 | SAL-ENC09-CE-01 | Abubaker | Power Module Stopped Working | Power Alarm | The power for the Power Module 1/2 interrupted and alarm cleared before FLM reaching the Site |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P3 - Medium | 2026-07-10 05:05 | 2026-07-10 05:06 | 1.3333 | 2026-07-10 05:05 | 2026-07-10 05:09 | 3.8667 | 3.8667 | alarm auto cleared before the FLM team reach the site | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | -
571 | Sirti-WAN-R3-Ticket-541 | NA | 2026-07-10 | DUK-ENC04-CE-01 | Abubaker | Link Down | LAN link down | Port GE 1/0/9 (Local Nodes) is down |  | Zone 80 | 25.3809325° 51.2215135° | Outside Doha | P3 - Medium | 2026-07-10 05:16 | 2026-07-10 05:25 | 8.65 | 2026-07-10 05:16 | 2026-07-10 06:53 | 96.85 | 96.85 | alarm auto cleared before the FLM team reach the site | Completed | Non-maintainer | 3rd Party | RMC | Alarm Cleared | -
572 | Sirti-WAN-R3-Ticket-542 | NA | 2026-07-10 | Duk-Enc06-CE-01 | Aaqib | Link Down | LAN link down | Port GE 1/0/9 (Local Nodes) is down |  | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | P3 - Medium | 2026-07-10 07:09 | 2026-07-10 07:12 | 3.5167 | 2026-07-10 07:12 | 2026-07-10 07:23 | 11 | 14.5167 | FLM replaced Ethernet cable connected to POE to CCTV , alarm is still flapping , issue is related to RMC which needs to check the CCTV | Completed | Non-maintainer | 3rd Party | RMC | Alarm Cleared | -
573 | Sirti-WAN-R3-Ticket-543 | NA | 2026-07-10 | COR-ENC12-CE-01 | Aaqib | VRRP Switchover | VRRP Switchover | VRRP is switching over due to LAN switch |  | Zone 61 | 25.324005699251956, 51.52792742883553 | Outside Doha | P3 - Medium | 2026-07-10 13:22 | 2026-07-10 13:26 | 4.0167 | 2026-07-10 13:22 | 2026-07-10 13:46 | 23.7333 | 23.7333 | Switchover performed due to LAN switch port flappping becasue of Hight temperature at LAN side. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
574 | Sirti-WAN-R3-Ticket-544 | NA | 2026-07-10 | P006-ENC17-UPE02 | Abubaker | CPU Temperature too High | High Temperature | High Temperature |  | Zone 56 | 25.19614, 51.45325 | Outside Doha | P3 - Medium | 2026-07-10 15:11 | 2026-07-10 15:22 | 10.8167 | 2026-07-10 15:11 | 2026-07-10 15:27 | 15.5 | 15.5 | alarm auto cleared before the FLM team reach the site, however the FLM team went to the site and did further inestigation, The AC unit was opened, and both the condenser and evaporator coils were chemically cleaned. The system was then recharged with R22 refrigerant, and the evaporator and compressor sensors were replaced with new ones and A/C replaced. After reassembly, the AC unit was tested and confirmed to be operating normally. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
575 | Sirti-WAN-R3-Ticket-545 | NA | 2026-07-11 | DUK-ENC12-CE-01 | Adel | High CRC errors on port GE1/0/9 | High CRC errors on port GE1/0/9 | CAT6 cable is damaged |  | Zone 72 | 25.4302156° 51.1497491° | Outside Doha | P4 - Low | 2026-07-11 00:54 | 2026-07-11 00:56 | 2 | 2026-07-11 01:08 | 2026-07-11 01:15 | 7 | 21.1167 | FLM replace damaged CAT6 cable with new one | Completed | Maintainer | N/A | N/A | Alarm Cleared | Rizwan
576 | Sirti-WAN-R3-Ticket-546 | NA | 2026-07-11 | DUK-ENC04-CE-01 | Adel | Link Down | LAN link down | Port GE 1/0/9 (Local Nodes) is down |  | Zone 80 | 25.3809325° 51.2215135° | Outside Doha | P3 - Medium | 2026-07-11 05:29 | 2026-07-11 05:33 | 4 | 2026-07-11 06:16 | 2026-07-11 06:38 | 22 | 69.0667 | The CAT6 cable was jacked out and plugged in again | Completed | Non-maintainer | 3rd Party | RMC | Alarm Cleared | Umair
577 | Sirti-WAN-R3-Ticket-547 | NA | 2026-07-12 | CRR-ENC37-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power inturruption |  | Zone 23 | 25.265846° 51.500562° | Inside Doha | P2 - High | 2026-07-12 21:41 | 2026-07-12 21:44 | 3 | 2026-07-12 21:41 | 2026-07-12 21:47 | 5.7667 | 5.7667 | kahromaa power inturruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
578 | Sirti-WAN-R3-Ticket-548 | NA | 2026-07-13 | P059C1-N3-ENC20-CE-01 | Sanket | Link Down | LAN link down | Port XGE 0/0/3 towards LAN ring 03 |  | Zone 70 | 25.44194931° 51.41112813° | Outside Doha | P3 - Medium | 2026-07-13 07:55 | 2026-07-13 08:02 | 6.4333 | 2026-07-13 08:09 | 2026-07-13 08:10 | 1.1167 | 14.7167 | The link is down towards LAN and Autorestored. | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | -
579 | Sirti-WAN-R3-Ticket-549 | NA | 2026-07-13 | P002-ENC14-UPE-02 | Sanket | CPU temperature too High | High Temperature | Ac compressor was overheating and not responding to cool |  | Zone 55 | 25.249527118° 51.47124863° | Outside Doha | P3 - Medium | 2026-07-13 14:26 | 2026-07-13 14:31 | 5.1167 | 2026-07-13 15:31 | 2026-07-13 15:34 | 3 | 67.6 | FLM Opened AC unit , cleaned all condenser and evaporator with chemical cleaning compressor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
580 | Sirti-WAN-R3-Ticket-550 | NA | 2026-07-13 | P029C1-ENC01-CE-01.omc.local | Adel | Link Down | LAN link down | LAN switch is hang |  | Zone 53 | 25.2721112° 51.4331388° | Outside Doha | P3 - Medium | 2026-07-13 17:49 | 2026-07-13 17:52 | 3 | 2026-07-13 19:10 | 2026-07-13 19:16 | 5.5667 | 86.95 | FLM Rebooted hanged LAN switch | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Irshad
581 | Sirti-WAN-R3-Ticket-551 | NA | 2026-07-13 | P008C2-ENC17-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Breaker was tripped inside the WAN cabinet |  | Zone 56 | 25.2323811° 51.5173691° | Outside Doha | P2 - High | 2026-07-13 18:43 | 2026-07-13 18:46 | 3 | 2026-07-13 19:11 | 2026-07-13 19:20 | 9 | 36.9833 | FLM switched on tripped Breaker inside the WAN cabinet | Completed | Maintainer | N/A | N/A | Device Restored | Najeeb
582 | Sirti-WAN-R3-Ticket-552 | NA | 2026-07-14 | RAA-TCR-CE-01 | Aaqib | Link Down | Link down towards Control Room | Port Ether-Trunk 01 connected to IE4K switch(RAA-Control Room) went down |  | Zone 18 | 25.2852478° 51.5517009° | Inside Doha | P3 - Medium | 2026-07-14 02:49 | 2026-07-14 02:51 | 1.4 | 2026-07-14 02:49 | 2026-07-14 02:52 | 2.8 | 2.8 | RAA-TCR-CE-01 Port Ether-Trunk 01 connected to IE4K switch(RAA-Control Room) went down and auto restored | Completed | Non-maintainer | 3rd Party | RAA Control Room | Alarm Cleared | -
583 | Sirti-WAN-R3-Ticket-553 | NA | 2026-07-14 | P029C1-ENC01-CE-01.omc.local | Sanket | Link Down | LAN link down | LAN switch is hang |  | Zone 53 | 25.2721112° 51.4331388° | Outside Doha | P3 - Medium | 2026-07-14 08:36 | 2026-07-14 08:49 | 13.7667 | 2026-07-14 09:10 | 2026-07-14 09:19 | 8.1667 | 42.9167 | FLM Rebooted hanged LAN switch | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Hichem
584 | Sirti-WAN-R3-Ticket-554 | NA | 2026-07-14 | P029C1-ENC01-CE-01.omc.local | Sanket | Link Down | LAN link down | LAN switch is hang |  | Zone 53 | 25.2721112° 51.4331388° | Outside Doha | P3 - Medium | 2026-07-14 10:28 | 2026-07-14 10:36 | 8.1167 | 2026-07-14 15:30 | 2026-07-14 16:27 | 56.8833 | 358.8 | FLM replaced faulty LAN switch | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Irshad
585 | Sirti-WAN-R3-Ticket-555 | NA | 2026-07-14 | P029C1-ENC01-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | FLM is replacing LAN switch in the cabinate |  | Zone 53 | 25.2721112° 51.4331388° | Outside Doha | P2 - High | 2026-07-14 16:10 | 2026-07-14 16:12 | 2 | 2026-07-14 16:10 | 2026-07-14 16:15 | 5.05 | 5.05 | FLM tripped CB while he is replacing LAN switch on site | Completed | Maintainer | N/A | N/A | Device Restored | Irshad
586 | Sirti-WAN-R3-Ticket-556 | NA | 2026-07-15 | P007C2-170018-R2-CSW | Sanket | Link Down | LAN link down | The STE team is working to reslve workstation issue which is connected to GE 1/0/18 and GE 2/0/16 |  | Zone 52 | 25.2942202 51.4657002 | Outside Doha | P3 - Medium | 2026-07-15 10:22 | 2026-07-15 10:30 | 8.4 | 2026-07-15 11:34 | 2026-07-15 11:49 | 14.8333 | 87.2333 | The STE team is working to reslve workstation issue which is connected to GE 1/0/18 and GE 2/0/16 (LAN) | Completed | Non-maintainer | 3rd Party | ST Engineering | Device Restored
587 | Sirti-WAN-R3-Ticket-557 | NA | 2026-07-15 | P010-ENC01-UPE01 | Abubaker | CPU temperature too High | High Temperature | Alarm Auto cleared before FLM reached the site |  | Zone 81 | 25.1398815° 51.4073931° | Outside Doha | P3 - Medium | 2026-07-15 15:43 | 2026-07-15 15:51 | 7.5167 | 2026-07-15 15:43 | 2026-07-15 15:52 | 9 | 9 | alarm auto cleared before the FLM team reach the site | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
588 | Sirti-WAN-R3-Ticket-558 | NA | 2026-07-15 | P002-ENC34-CE-01 | Abubaker | Link Down | LAN link down | Alarm Auto cleared before FLM reached the site |  | Zone56 | 25.2292791° 51.4377406° | Outside Doha | P3 - Medium | 2026-07-15 16:35 | 2026-07-15 16:42 | 6.9 | 2026-07-15 16:35 | 2026-07-15 16:42 | 6.8167 | 6.8167 | alarm auto cleared before the FLM team reach the site | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | -
589 | Sirti-WAN-R3-Ticket-559 | NA | 2026-07-15 | P007C2-ENC55-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Breaker was tripped inside the WAN cabinet |  | Zone54 | 25.2868875° 51.466039° | Outside Doha | P2 - High | 2026-07-15 18:23 | 2026-07-15 18:25 | 2.3833 | 2026-07-15 18:57 | 2026-07-15 19:08 | 10.8833 | 45.2667 | FLM Checked the input and output voltage and switched on the tripped Circuit Breaker inside the WAN cabinet | Completed | Maintainer | N/A | N/A | Device Restored | Najeeb
590 | Sirti-WAN-R3-Ticket-560 | NA | 2026-07-15 | P003-ENC42-CE-DGME-01.omc.local | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Breaker was tripped inside the WAN cabinet |  | Zone65 | 25.3300858° 51.5170897° | Inside Doha | P2 - High | 2026-07-15 21:01 | 2026-07-15 21:04 | 3.3167 | 2026-07-15 21:49 | 2026-07-15 22:00 | 11.8167 | 59.7833 | FLM Checked the input and output voltage and switched on the tripped Circuit Breaker inside the WAN cabinet | Completed | Maintainer | N/A | N/A | Device Restored | Hassan
591 | Sirti-WAN-R3-Ticket-561 | NA | 2026-07-17 | SAL-TCC-NPE-01 | Adel | Link Down | WAN Link down (100GE1/5/0/2) to P012-ENC09-UPE01 | link is auto restored |  | Zone55 | 25.2088874° 51.4008611° | Outside Doha | P3 - Medium | 2026-07-17 13:58 | 2026-07-17 14:00 | 2 | 2026-07-17 13:58 | 2026-07-17 14:29 | 31.0333 | 31.0333 | link is auto restored | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
592 | Sirti-WAN-R3-Ticket-562 | NA | 2026-07-17 | P059C1-N2-ENC01-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone30 | 25.3558071° 51.45176723° | Outside Doha | P2 - High | 2026-07-17 17:10 | 2026-07-17 17:13 | 2.8333 | 2026-07-17 17:10 | 2026-07-17 17:16 | 6.1167 | 6.1167 | kahromaa power inturruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
593 | Sirti-WAN-R3-Ticket-563 | NA | 2026-07-17 | SAL-TCC-NPE-01 | Abubaker | Link Down | WAN Link down (100GE1/5/0/2) to P012-ENC09-UPE01 | link is auto restored |  | Zone55 | 25.2088874° 51.4008611° | Outside Doha | P3 - Medium | 2026-07-17 18:55 | 2026-07-17 19:00 | 4.6167 | 2026-07-17 18:55 | 2026-07-17 19:15 | 19.65 | 19.65 | link is auto restored before FLM reaching the site | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
594 | Sirti-WAN-R3-Ticket-564 | NA | 2026-07-17 | P059C1-N2-ENC01-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone30 | 25.3558071° 51.45176723° | Outside Doha | P2 - High | 2026-07-17 19:58 | 2026-07-17 20:05 | 6.8167 | 2026-07-17 19:58 | 2026-07-17 20:06 | 8.2667 | 8.2667 | kahromaa power inturruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
595 | Sirti-WAN-R3-Ticket-565 | NA | 2026-07-18 | SAL-ENC14-CE-01 | Aaqib | Link Down | LAN link down | Port 25GE 1/0/4 (LAN-Ring-02) down towards LAN |  | Zone55 | 25.1858801° 51.3628538° | Outside Doha | P3 - Medium | 2026-07-18 05:17 | 2026-07-18 05:20 | 3 | 2026-07-18 05:17 | 2026-07-18 06:21 | 64.6167 | 64.6167 | Main three pole MCB Breakers was tripped , FLM switched it on and LAN node is back online | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Samad
596 | Sirti-WAN-R3-Ticket-566 | NA | 2026-07-18 | SAL-TCC-NPE-01 | Adel | Link Down | WAN Link down (100GE1/5/0/2) to P012-ENC09-UPE01 | link is auto restored |  | Zone55 | 25.2088874° 51.4008611° | Outside Doha | P3 - Medium | 2026-07-18 13:30 | 2026-07-18 13:34 | 4 | 2026-07-18 14:11 | 2026-07-18 14:14 | 3 | 44 | link is auto restored, Access permission is requested for accessing SAL-TCC server room | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
597 | Sirti-WAN-R3-Ticket-567 | NA | 2026-07-18 | SAL-TCC-NPE-01 | Abubaker | Link Down | WAN Link down (100GE1/5/0/2) to P012-ENC09-UPE01 | link is auto restored |  | Zone55 | 25.2088874° 51.4008611° | Outside Doha | P3 - Medium | 2026-07-18 18:53 | 2026-07-18 18:57 | 3.6667 | 2026-07-18 18:53 | 2026-07-18 19:30 | 37 | 37 | link is auto restored, Access permission is requested for accessing SAL-TCC server room | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
598 | Sirti-WAN-R3-Ticket-568 | NA | 2026-07-18 | P023C1-ENC01-CE-01 | Abubaker | Link Down | LAN link down | LAN device connected to Port Te 1/27 is down due to power outage |  | Zone90 | 25.111748° 51.583897° | Outside Doha | P3 - Medium | 2026-07-18 19:11 | 2026-07-18 19:15 | 3.9833 | 2026-07-18 20:17 | 2026-07-19 02:58 | 401.2333 | 467.15 | LAN team coordinated with KAHRAMAA to recover the power and powered on the LAN deviceand port become up | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
599 | Sirti-WAN-R3-Ticket-569 | NA | 2026-07-19 | P003-ENC40-UPE-02 | Adel | Power Module Stopped Working | power Alarm | kahromaa Team activity near the cabinet |  | Zone63 | 25.3344995° 51.5180512° | Outside Doha | P3 - Medium | 2026-07-19 09:09 | 2026-07-19 09:11 | 2 | 2026-07-19 09:37 | 2026-07-19 11:17 | 100.1333 | 128.1333 | Durking kahromaa Team activity near the cabinet ,one phase is missed , after activity completed power is restored | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | Eric
600 | Sirti-WAN-R3-Ticket-570 | NA | 2026-07-19 | P003-ENC40-UPE-02 P003-ENC40-CE-DGME-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA team was working at the same area |  | Zone63 | 25.3344995° 51.5180512° | Outside Doha | P2 - High | 2026-07-19 10:40 | 2026-07-19 10:43 | 3.15 | 2026-07-19 10:40 | 2026-07-19 10:45 | 5 | 5 | After KAHRAMAA team completed their activity the power recovered and devices restored | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
601 | Sirti-WAN-R3-Ticket-571 | NA | 2026-07-19 | DUK-DBR-UPE-01 DUK-DBR-USG-01 DUK-DBR-USG-02 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no kharomaa power inside the shelter |  | Zone80 | 25.377556, 51.228333 | Outside Doha | P2 - High | 2026-07-19 11:51 | 2026-07-19 11:56 | 4.9167 | 2026-07-19 12:30 | 2026-07-19 13:06 | 36 | 75.3 | FLM found main CB was tripped inside the shelter and the FP , FLM switched them on , site is stable | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Ahmed
602 | Sirti-WAN-R3-Ticket-572 | NA | 2026-07-19 | SAL-TCC-NPE-01 | Adel | Link Down | WAN Link down (100GE1/5/0/2) to P012-ENC09-UPE01 | link is auto restored |  | Zone55 | 25.2088874° 51.4008611° | Outside Doha | P3 - Medium | 2026-07-19 12:33 | 2026-07-19 12:36 | 3 | 2026-07-19 12:33 | 2026-07-19 12:55 | 21.9833 | 21.9833 | link is auto restored before FLM reaching the site | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
603 | Sirti-WAN-R3-Ticket-573 | NA | 2026-07-19 | P010-ENC89-UPE-02 | Adel | CPU temperature too High | High Temperature | The AC was operating, but it was not providing proper cooling. |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | P3 - Medium | 2026-07-19 13:00 | 2026-07-19 13:05 | 5.1 | 2026-07-19 13:00 | 2026-07-19 17:58 | 298.3333 | 298.3333 | A faulty condenser fan was identified as the cause of the high-temperature alarm. The fan was replaced with a new unit | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
604 | Sirti-WAN-R3-Ticket-574 | NA | 2026-07-19 | SAL-TCC-NPE-01 | Abubaker | Link Down | WAN Link down (100GE1/5/0/2) _ P012-ENC09-UPE01(100GE1/0/1) | link is auto restored |  | Zone55 | 25.2088874° 51.4008611° | Outside Doha | P3 - Medium | 2026-07-19 22:19 | 2026-07-19 22:21 | 1.9167 | 2026-07-19 22:19 | 2026-07-19 22:52 | 33.2667 | 33.2667 | link is auto restored before FLM reaching the site | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
605 | Sirti-WAN-R3-Ticket-575 | 27340228 | 2026-07-20 | P015-ENC22B-UPE-02 P015-ENC93-CE-01 P015-ENC22B-CE-01 P015-ENC80A-CE-01 P015-ENC18-CE-01 P015-ENC19A-CE-01 P015-ENC22A-CE-01 P015-ENC24A-CE-01 P015-ENC56-CE-01 P023C1-ENC01-UPE-01 P023C1-ENC05-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa outage |  | Zone 90 | 25.1313451° 51.5849661° | Outside Doha | P1 - Critical | 2026-07-20 08:50 | 2026-07-20 08:51 | 1 | 2026-07-20 09:20 | 2026-07-20 10:06 | 45.2833 | 75.2833 | Devices were down due to Kharahma major outage -Lock down in multiple sites which affected multiple nodes as well as the ring protection | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Farouq
606 | Sirti-WAN-R3-Ticket-576 | NA | 2026-07-20 | P060-TCR-NPE-01 | Adel | Power Module Stopped Working | power alarm | confirmed with tunnel team , power test activity is running |  | Zone55 | 25.545418° 51.446774° | Outside Doha | P3 - Medium | 2026-07-20 10:28 | 2026-07-20 10:29 | 1 | 2026-07-20 10:28 | 2026-07-20 10:28 | 0.66667 | 0.66667 | confermed with tunnel team , power test activity is running | Completed | Non-maintainer | 3rd Party | contractor | Alarm Cleared | -
607 | Sirti-WAN-R3-Ticket-577 | NA | 2026-07-20 | P007C2-ENC99-UPE-02 | Adel | CPU temperature too High | temperature alarm | high temperature inside the cabinet due to blockage and dust on the AC filters and condenser . |  | Zone52 | 25.2967109° 51.4488814° | Outside Doha | P3 - Medium | 2026-07-20 12:32 | 2026-07-20 12:34 | 2 | 2026-07-20 15:38 | 2026-07-20 15:43 | 4.8 | 191 | Visited the site and inspected the AC unit. Checked the power supply, cables, and voltage, and confirmed they were within the normal range. Found the AC filters and condenser heavily clogged with dust. Cleaned the filters and condenser using a blower, cloth towels, and water service. After cleaning, tested the AC unit and confirmed it was cooling properly and operating normally. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
608 | Sirti-WAN-R3-Ticket-578 | NA | 2026-07-20 | P017C2-ENC23-CE-01.omc.local | Adel | LAN Link Down | link down | LAN device is Down |  | Zone57 | 25.1702778° 51.4710278° | Outside Doha | P3 - Medium | 2026-07-20 13:47 | 2026-07-20 13:49 | 2 | 2026-07-20 16:52 | 2026-07-21 03:18 | 626 | 811.5833 | FLM Team replaced the PSU of the LAN switch and switched on the LAN device. The Port Changed at WAN switch | Completed | Non-maintainer | Node Up | N/A | Alarm Cleared | Suhail
609 | Sirti-WAN-R3-Ticket-579 | NA | 2026-07-20 | 22FEB-ENC25-UPE-02 | Adel | CPU temperature too High | temperature alarm | Refilling of R 134A gas |  | Zone51 | 25.31832397° 51.47088144° | Outside Doha | P3 - Medium | 2026-07-20 13:55 | 2026-07-20 13:57 | 2 | 2026-07-20 13:55 | 2026-07-20 14:16 | 20.8333 | 20.8333 | Visited the site and checked the power supply, cables, and voltage. Found a leak in the AC compressor pipe. Removed, cleaned with nitrogen, and repaired the pipe by brazing. Refilled the system with R-134a refrigerant, cleaned the AC unit, and tested its operation. The unit is now cooling properly. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
610 | Sirti-WAN-R3-Ticket-580 | NA | 2026-07-20 | CRR-ENC16-UPE-01 | Abubaker | CPU temperature too High | temperature alarm | Alarm Auto cleared before FLM reach the site |  | Zone42 | 25.2590324° 51.537498° | Inside Doha | P3 - Medium | 2026-07-20 14:47 | 2026-07-20 14:55 | 7.6167 | 2026-07-20 14:47 | 2026-07-20 16:47 | 119.3333 | 119.3333 | The air filter, evaporator coil, and condenser coil were found blocked and were thoroughly cleaned and washed. The refrigerant gas level was found low and was refilled. The thermostat was adjusted | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
611 | Sirti-WAN-R3-Ticket-581 | NA | 2026-07-20 | P010-ENC01-UPE01 | Abubaker | CPU temperature too High | temperature alarm | Alarm Auto cleared before FLM reach the site |  | Zone81 | 25.1398815° 51.4073931° | Outside Doha | P3 - Medium | 2026-07-20 16:47 | 2026-07-20 16:56 | 8.95 | 2026-07-20 16:47 | 2026-07-20 17:04 | 17.3333 | 17.3333 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
612 | Sirti-WAN-R3-Ticket-582 | NA | 2026-07-20 | P017C2-ENC23-CE-01.omc.local | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | kahramaa power inturruption |  | Zone57 | 25.1702778° 51.4710278° | Outside Doha | P2 - High | 2026-07-20 19:56 | 2026-07-20 19:58 | 1.7333 | 2026-07-20 19:56 | 2026-07-20 20:02 | 5.4667 | 5.4667 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
613 | Sirti-WAN-R3-Ticket-583 | NA | 2026-07-21 | SAL-TCC-NPE-01 | Sanket | Link Down | WAN Link down (100GE1/5/0/2) _ P012-ENC09-UPE01(100GE1/0/1) | link is auto restored |  | Zone56 | 25.2288° 51.5072° | Outside Doha | P3 - Medium | 2026-07-21 01:15 | 2026-07-21 01:26 | 10.3667 | 2026-07-21 02:24 | 2026-07-21 02:25 | 1 | 70.1 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared
614 | Sirti-WAN-R3-Ticket-584 | NA | 2026-07-21 | P059C1-N3-Enc33-CE-01 | Aaqib | Link Down | LAN link down and auto restored | Port XGE 0/0/3 (LAN-Ring-03) towards LAN |  | Zone70 | 25.53313695° 51.41207372° | Outside Doha | P3 - Medium | 2026-07-21 08:05 | 2026-07-21 08:07 | 2.25 | 2026-07-21 08:05 | 2026-07-21 08:24 | 19.1 | 19.1 | link is auto restored | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared
615 | Sirti-WAN-R3-Ticket-585 | NA | 2026-07-21 | P008C2-ENC33-CE-01 | Adel | LAN Link Down | link down | SCADA switch is hanged |  | Zone44 | 25.2377365° 51.5294852° | Outside Doha | P3 - Medium | 2026-07-21 17:15 | 2026-07-21 17:18 | 3 | 2026-07-21 18:30 | 2026-07-22 20:00 | 1530 | 1604.6333 | flm Replaced the faulty cisco switch with new BDcomm one | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | najeeb
616 | Sirti-WAN-R3-Ticket-586 | NA | 2026-07-21 | P007C5P1-ENC30-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kahromaa power inturruption |  | Zone55 | 25.2725257° 51.4827063° | Outside Doha | P2 - High | 2026-07-21 21:11 | 2026-07-21 21:12 | 1 | 2026-07-21 21:11 | 2026-07-21 21:18 | 6.5333 | 6.5333 | Kahromaa power inturruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
617 | Sirti-WAN-R3-Ticket-587 | NA | 2026-07-22 | P059C1-N3-Enc33-CE-01 | Aaqib | Link Down | LAN link down | Port XGE 0/0/2 (LAN-Ring-02) towards LAN |  | Zone70 | 25.53313695° 51.41207372° | Outside Doha | P3 - Medium | 2026-07-22 07:06 | 2026-07-22 07:10 | 3.1833 | 2026-07-22 08:01 | 2026-07-22 08:27 | 25.25 | 80.2 | kahramaa power inturruption at LAN side | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared
618 | Sirti-WAN-R3-Ticket-588 | NA | 2026-07-22 | CRR-ENC24-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa power inturruption |  | Zone23 | 25.27181° 51.51094° | Inside Doha | P2 - High | 2026-07-22 08:08 | 2026-07-22 08:12 | 3.2167 | 2026-07-22 08:08 | 2026-07-22 08:13 | 5.0167 | 5.0167 | kahramaa power inturruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
619 | Sirti-WAN-R3-Ticket-589 | NA | 2026-07-22 | P059C1-N3-ENC33-CE-01 | Adel | Link Down | LAN link down | CB was tripped for LAN cabinet that connected to FP of the street signal |  | Zone70 | 25.53313695° 51.41207372° | Outside Doha | P3 - Medium | 2026-07-22 16:33 | 2026-07-22 16:34 | 1 | 2026-07-22 17:19 | 2026-07-22 17:35 | 16 | 61.5333 | Kahromaa team switched on power at street signal FP | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | Sanjeewa
620 | Sirti-WAN-R3-Ticket-590 | NA | 2026-07-22 | P002-ENC07-UPE-01 | Adel | physical board issue | Card Stopped working | alarm is active on the card |  | Zone55 | 25.257° 51.486° | Outside Doha | P3 - Medium | 2026-07-22 18:35 | 2026-07-22 18:36 | 1 | 2026-07-22 18:36 | 2026-07-22 18:40 | 4 | 5 | FLM reset the board slot # 3 at UPE , after reseting the alarm is cleared from the board | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Hassan
621 | Sirti-WAN-R3-Ticket-591 | NA | 2026-07-22 | P017C2-ENC23-CE-01.omc.local | Adel | Link Down | LAN link down | port is in error-disabled mode |  | Zone57 | 25.1702778° 51.4710278° | Outside Doha | P3 - Medium | 2026-07-22 22:12 | 2026-07-22 22:14 | 2 | 2026-07-22 22:14 | 2026-07-22 22:38 | 24.3667 | 26.3667 | NOC team reconfigured the port to set it up | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Hassan
622 | Sirti-WAN-R3-Ticket-592 | NA | 2026-07-23 | P004-ENC43-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC is not cooling |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-07-23 12:24 | 2026-07-23 12:30 | 6.7 | 2026-07-23 15:30 | 2026-07-23 16:41 | 70.5833 | 257.0833 | Found an AC condenser pipe leak and a faulty AC sensor. Repaired the pipe by brazing, replaced the 35 µF capacitor, installed a new exhaust gas sensor, refilled R22A refrigerant, and cleaned the AC unit. Switched on the AC breaker and confirmed the AC was cooling normally. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Patrick
623 | Sirti-WAN-R3-Ticket-593 | NA | 2026-07-23 | P008C2-ENC42-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB is tripped inside ITS cabinet ,due to short circuit of aircondition |  | Zone 56 | 25.211892° 51.5391135° | Inside Doha | P2 - High | 2026-07-23 12:49 | 2026-07-23 12:54 | 5 | 2026-07-23 15:30 | 2026-07-23 15:41 | 10.7667 | 171.4333 | FLM switched on tripped CB inside ITS cabinet , AC team will check AC . Performed general servicing of the AC unit, including cleaning the condenser coil and air filter, washing the unit, and checking and adjusting the thermostat for proper operation | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | irshad
624 | Sirti-WAN-R3-Ticket-594 | NA | 2026-07-23 | P023C2-Enc43-CE-01 | Aaqib | Link Down | LAN link down | XGE 1/0/4 connected towards LAN(USW-4) is down |  | Zone 82 | 25.1701761 51.3230788 | Outside Doha | P3 - Medium | 2026-07-23 12:38 | 2026-07-23 12:41 | 3.75 | 2026-07-23 12:38 | 2026-07-23 13:31 | 52.9833 | 52.9833 | Switch towards LAN restored automatically | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
625 | Sirti-WAN-R3-Ticket-595 | NA | 2026-07-23 | 22FEB-ENC25-UPE-02 | Aaqib | CPU temperature too High | High Temperature | AC is not cooling |  | Zone51 | 25.31832397° 51.47088144° | Outside Doha | P3 - Medium | 2026-07-23 14:14 | 2026-07-23 14:18 | 4.0167 | 2026-07-23 15:50 | 2026-07-23 16:52 | 61.5667 | 157.8167 | FLM add gas to AC as gas level was low | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | khadar
626 | Sirti-WAN-R3-Ticket-596 | NA | 2026-07-23 | P023C2-Enc43-CE-01 | Adel | Link Down | LAN link down | XGE 1/0/4 connected towards LAN(USW-4) is down |  | Zone 82 | 25.1701761 51.3230788 | Outside Doha | P3 - Medium | 2026-07-23 14:52 | 2026-07-23 14:55 | 3.0167 | 2026-07-23 16:31 | 2026-07-23 16:55 | 24 | 122.5333 | LAN switch was hanged due to high temp , FLM restarted it | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
627 | Sirti-WAN-R3-Ticket-597 | NA | 2026-07-23 | P004-ENC43-UPE-02 P004-ENC43-CE-01 P023C2-ENC43-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P2 - High | 2026-07-23 16:55 | 2026-07-23 16:57 | 2 | 2026-07-23 16:55 | 2026-07-23 17:01 | 5.4167 | 5.4167 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | -
628 | Sirti-WAN-R3-Ticket-598 | NA | 2026-07-24 | P007C2-ENC100-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | UPS input breaker was tripped |  | Zone 53 | 25.29725° 51.444408° | Outside Doha | P2 - High | 2026-07-24 06:10 | 2026-07-24 06:17 | 7.0667 | 2026-07-24 07:16 | 2026-07-24 07:44 | 28.6667 | 94 | UPS Breaker was tripped | Completed | Non-maintainer | defect | UPS | Device Restored
629 | Sirti-WAN-R3-Ticket-599 | NA | 2026-07-24 | P004-MOQ-CE-01 P004-MOQ-USG-01 P004-MOQ-USG-02 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Batteries were drain due to UPS issue |  | Zone 53 | 25.319385° 51.352255° | Outside Doha | P1 - Critical | 2026-07-24 06:46 | 2026-07-24 06:48 | 2.3 | 2026-07-24 06:46 | 2026-07-24 06:57 | 11.4167 | 11.4167 | As per GDBG tunnel team, Batteries were drain due to UPS issue, causing device to be down. Devices are restored and alarms are clear for now | Completed | Non-maintainer | 3rd Party | GDBG Control Room | Device Restored | -
630 | Sirti-WAN-R3-Ticket-599 | NA | 2026-07-24 | P004 DWDM P004-TMC-NPE-01 | Aaqib | Power Module Stopped Working | Power Alarm at Modules 1,3,5 | Batteries were drain due to UPS issue |  | Zone 53 | 25.319385° 51.352255° | Outside Doha | P3 - Medium | 2026-07-24 06:46 | 2026-07-24 06:48 | 2.3 | 2026-07-24 06:46 | 2026-07-24 06:57 | 11.4167 | 11.4167 | As per GDBG tunnel team, Batteries were drain due to UPS issue, causing device to be down. Devices are restored and alarms are clear for now | Completed | Non-maintainer | 3rd Party | GDBG Control Room | Alarm Cleared
631 | Sirti-WAN-R3-Ticket-600 | NA | 2026-07-24 | P023C2-Enc43-CE-01 | Aaqib | Link Down | LAN link down | XGE 1/0/4 connected towards LAN(USW-4) is down |  | Zone 82 | 25.1701761 51.3230788 | Outside Doha | P3 - Medium | 2026-07-24 07:03 | 2026-07-24 07:05 | 2.5833 | 2026-07-24 07:03 | 2026-07-24 07:48 | 45.3 | 45.3 | Link is connected to LAN switch and the switch was hanged due to high temp , FLM open the cabinet door. | Completed | Non-maintainer | defect | AC | Alarm Cleared
632 | Sirti-WAN-R3-Ticket-601 | 27429318 | 2026-07-24 | P004-MOQ-CE-01 P004-MOQ-USG-01 P004-MOQ-USG-02 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | All systems at QMT are down due to high temperature in the UPS room |  | Zone 53 | 25.319385° 51.352255° | Outside Doha | P1 - Critical | 2026-07-24 08:40 | 2026-07-24 08:42 | 2.3667 | 2026-07-24 09:36 | 2026-07-24 09:55 | 19.3167 | 75.3667 | The outage was caused by high temperature in the UPS room, which affected UPS operation and resulted in the shutdown of all systems. The UPS was isolated by GDBG team, and the load was successfully bypassed to the Khahrama supply, restoring all services. The HVAC issue is being addressed to prevent recurrence. Official RCA yet to be shared by GDBG | Completed | Non-maintainer | 3rd Party | GDBG Control Room | Device Restored
633 | Sirti-WAN-R3-Ticket-601 | NA | 2026-07-24 | P004 DWDM P004-TMC-NPE-01 | Aaqib | Power Module Stopped Working | P004 DWDM (Pri and Sec) P004-TMC-NPE-01 (Pwr2,5,6 Main Chasis) (Pwr1,3,4 Secondary Chasis) Power modules are down | All systems at QMT are down due to high temperature in the UPS room |  | Zone 53 | 25.319385° 51.352255° | Outside Doha | P3 - Medium | 2026-07-24 08:40 | 2026-07-24 08:42 | 2.3667 | 2026-07-24 09:36 | 2026-07-24 09:55 | 19.3167 | 75.3667 | The outage was caused by high temperature in the UPS room, which affected UPS operation and resulted in the shutdown of all systems. The UPS was isolated by GDBG team, and the load was successfully bypassed to the Khahrama supply, restoring all services. The HVAC issue is being addressed to prevent recurrence. Official RCA yet to be shared by GDBG | Completed | Non-maintainer | 3rd Party | GDBG Control Room | Alarm Cleared
634 | Sirti-WAN-R3-Ticket-602 | NA | 2026-07-24 | P007C2-ENC71-CE-01 | Aaqib | Link Down | Port Te 1/26 LAN link down due to UPS tripping and high temperature at P007C2-Enc100 | UPS Input breaker was found tripped due to high temperature |  | Zone 53 | 25.2915066° 51.4411072° | Outside Doha | P3 - Medium | 2026-07-24 08:33 | 2026-07-24 08:36 | 3.05 | 2026-07-24 09:02 | 2026-07-24 09:13 | 10.6333 | 40 | UPS Input breaker was tripped due to high temperature inside LAN Cabinet. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
635 | Sirti-WAN-R3-Ticket-602 | NA | 2026-07-24 | P007C2-ENC82-CE-01 | Aaqib | Link Down | Port Te 1/25 WAN link down due to UPS tripping and high temperature at P007C2-Enc100 | UPS Input breaker was found tripped due to high temperature |  | Zone 52 | 25.3045066° 51.4548113° | Outside Doha | P3 - Medium | 2026-07-24 08:33 | 2026-07-24 08:36 | 3.05 | 2026-07-24 09:02 | 2026-07-24 09:13 | 10.6333 | 40 | UPS Input breaker was tripped due to high temperature inside LAN Cabinet. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
636 | Sirti-WAN-R3-Ticket-602 | NA | 2026-07-24 | P007C2-ENC25-CE-01 | Aaqib | Link Down | Port Te 1/25 LAN link down due to UPS tripping and high temperature at P007C2-Enc100 | UPS Input breaker was found tripped due to high temperature |  | Zone 52 | 25.294605° 51.463683° | Outside Doha | P3 - Medium | 2026-07-24 08:33 | 2026-07-24 08:36 | 3.05 | 2026-07-24 09:02 | 2026-07-24 09:13 | 10.6333 | 40 | UPS Input breaker was tripped due to high temperature inside LAN Cabinet. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
637 | Sirti-WAN-R3-Ticket-602 | NA | 2026-07-24 | P007C2-ENC25-CE-01 | Aaqib | Link Down | Port Gi 1/13 LAN link down due to UPS tripping and high temperature at P007C2-Enc100 | UPS Input breaker was found tripped due to high temperature |  | Zone 52 | 25.294605° 51.463683° | Outside Doha | P3 - Medium | 2026-07-24 08:33 | 2026-07-24 08:36 | 3.05 | 2026-07-24 09:02 | 2026-07-24 09:13 | 10.6333 | 40 | UPS Input breaker was tripped due to high temperature inside LAN Cabinet. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
638 | Sirti-WAN-R3-Ticket-602 | NA | 2026-07-24 | P007C2-ENC99-CE-01 | Aaqib | Link Down | Port Te 1/23 LAN link down due to UPS tripping and high temperature at P007C2-Enc100 | UPS Input breaker was found tripped due to high temperature |  | Zone 52 | 25.2967109° 51.4488814° | Outside Doha | P3 - Medium | 2026-07-24 08:33 | 2026-07-24 08:36 | 3.05 | 2026-07-24 09:02 | 2026-07-24 09:13 | 10.6333 | 40 | UPS Input breaker was tripped due to high temperature inside LAN Cabinet. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
639 | Sirti-WAN-R3-Ticket-602 | NA | 2026-07-24 | P007C2-ENC49-CE-01 | Aaqib | Link Down | Port Te 1/23 WAN link down due to UPS tripping and high temperature at P007C2-Enc100 | UPS Input breaker was found tripped due to high temperature |  | Zone 52 | 25.2988947° 51.438492° | Outside Doha | P3 - Medium | 2026-07-24 08:33 | 2026-07-24 08:36 | 3.05 | 2026-07-24 09:02 | 2026-07-24 09:13 | 10.6333 | 40 | UPS Input breaker was tripped due to high temperature inside LAN Cabinet. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
640 | Sirti-WAN-R3-Ticket-603 | NA | 2026-07-24 | DUK-ENC30-CE-01 | Aaqib | CPU temperature too High | High Temperature | condenser fan is faulty |  | Zone 85 | 25.4637854° 50.930279° | Outside Doha | P3 - Medium | 2026-07-24 14:18 | 2026-07-24 14:24 | 5.3333 | 2026-07-24 16:50 | 2026-07-24 17:05 | 15.2667 | 166.7833 | FLM replaced the defective condenser fan with a new one. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
641 | Sirti-WAN-R3-Ticket-604 | NA | 2026-07-24 | P059C1-ENC20-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 70 | 25.44194931° 51.41112813° | Outside Doha | P2 - High | 2026-07-24 16:22 | 2026-07-24 16:23 | 1 | 2026-07-24 16:22 | 2026-07-24 16:28 | 6.1333 | 6.1333 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored
642 | Sirti-WAN-R3-Ticket-605 | NA | 2026-07-24 | P004-ENC43-UPE-02 P004-ENC43-CE-01 P023C2-ENC43-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P2 - High | 2026-07-24 16:18 | 2026-07-24 16:19 | 1 | 2026-07-24 16:18 | 2026-07-24 16:40 | 21.35 | 21.35 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored
643 | Sirti-WAN-R3-Ticket-606 | NA | 2026-07-24 | P060-ENC38-CE-GME-04 | Sanket | Link Down | WAN Link Down | 10G Link down P060-ENC38-CE-GME-04 towards P0060-ENC56CE-DGME-01 .Tthe patch cord was slightly bent |  | Zone 69 | 25.4311454° 51.4832727° | Outside Doha | P3 - Medium | 2026-07-24 23:37 | 2026-07-24 23:40 | 3.1833 | 2026-07-25 00:10 | 2026-07-25 00:16 | 5.9 | 39.2333 | the patch cord was slightly bent. Removed the bend from the patch cord and reconnected it. | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Rizwan
644 | Sirti-WAN-R3-Ticket-607 | NA | 2026-07-25 | P060-ENC38-CE-GME-04 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 69 | 25.4311454° 51.4832727° | Outside Doha | P2 - High | 2026-07-25 00:21 | 2026-07-25 00:22 | 1 | 2026-07-25 00:25 | 2026-07-25 00:27 | 2 | 5.1667 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Rizwan
645 | Sirti-WAN-R3-Ticket-608 | NA | 2026-07-25 | P012-ENC30-NPE-01 | Sanket | Link Down | WAN Link Down | 100G link down at P012-ENC30-NPE-01 towards P017C1-ENC01-UPE-01 due to FIber Patch chord issue. |  | Zone 56 | 25.2162349° 51.5021362° | Outside Doha | P3 - Medium | 2026-07-25 04:48 | 2026-07-25 04:54 | 6.3833 | 2026-07-25 05:56 | 2026-07-25 06:59 | 63.0167 | 131.45 | Bent fiber patch cable identified at P017C2-ENC01-UPE-01.Replaced the damaged fiber cable | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Suhail/Hichem
646 | Sirti-WAN-R3-Ticket-609 | 27479901 | 2026-07-25 | SAL-ENC04-UPE-01 SAL-ENC04-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | no power |  | Zone 57 | 25.2204517° 51.4230388° | Outside Doha | P2 - High | 2026-07-25 19:20 | 2026-07-25 19:23 | 3 | 2026-07-25 20:00 | 2026-07-25 23:16 | 196.0667 | 236.5 | Kahramaa Issue | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Hassan
647 | Sirti-WAN-R3-Ticket-610 | NA | 2026-07-25 | P017C2-ENC23-CE-01.omc.local | Abubaker | Link Down | LAN Link Down | Port Gi1/16 toward LAN device is down |  | Zone 57 | 25.1702778° 51.4710278° | Outside Doha | P3 - Medium | 2026-07-25 23:28 | 2026-07-25 23:35 | 7.2 | 2026-07-26 00:28 | 2026-07-26 00:38 | 10.2 | 70.0833 |  | Completed | Maintainer | N/A | N/A | Alarm Cleared | Hassan
648 | Sirti-WAN-R3-Ticket-611 | NA | 2026-07-26 | IE5000-6009.ashghal | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | KAHRAMAA power interruption |  | Zone 61 | 25.3233945337, 51.5360444444 | Inside Doha | P2 - High | 2026-07-26 05:57 | 2026-07-26 05:59 | 2.1333 | 2026-07-26 05:57 | 2026-07-26 06:00 | 3.5833 | 3.5833 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
649 | Sirti-WAN-R3-Ticket-612 | NA | 2026-07-26 | P059C1-N3-ENC33-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | Device was down due QBC (Egis) power team working at street lights FP |  | Zone 70 | 25.53313695° 51.41207372° | Outside Doha | P2 - High | 2026-07-26 07:45 | 2026-07-26 07:49 | 4.5333 | 2026-07-26 08:44 | 2026-07-26 09:02 | 18.15 | 77.0833 | Device was down due QBC (Egis) power team working at street lights FP | Completed | Non-maintainer | 3rd Party | QBC(EGIS) | Device Restored | Hichem
650 | Sirti-WAN-R3-Ticket-613 | NA | 2026-07-26 | SAL-ENC04-UPE-01 SAL-ENC04-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | Khahrama team is working on site |  | Zone 57 | 25.2204517° 51.4230388° | Outside Doha | P2 - High | 2026-07-26 11:09 | 2026-07-26 11:10 | 1.35 | 2026-07-26 11:09 | 2026-07-27 08:18 | 1269.2333 | 1269.2333 | Car Accident of the SLFP and Kahramaa Cabinets, No FP-ITS | Completed | Non-maintainer | 3rd Party | RF001, Kahramaa | Device Restored | khadar
651 | Sirti-WAN-R3-Ticket-614 | NA | 2026-07-26 | P023C1-ENC01-CE-01 | Adel | Link Down | LAN Link Down | CB is tripped inside LAN cabinet |  | Zone 90 | 25.111748° 51.583897° | Outside Doha | P3 - Medium | 2026-07-26 18:15 | 2026-07-26 18:18 | 3 | 2026-07-26 19:31 | 2026-07-26 19:44 | 13 | 88.5 | FLM Switched on tripped CB inside LAN cabinet | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Najeeb
652 | Sirti-WAN-R3-Ticket-615 | NA | 2026-07-26 | P059C1-ENC51-CE-01 | Adel | optical model temprature too high | high Temperature | AC CB was tripped |  | Zone 71 | 25.624509° 51.39970937° | Outside Doha | P3 - Medium | 2026-07-26 15:00 | 2026-07-26 15:02 | 2 | 2026-07-26 20:15 | 2026-07-26 20:23 | 8 | 322.6 | FLM Switched on tripped Aircondition CB inside cabinet | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Farouq
653 | Sirti-WAN-R3-Ticket-616 | NA | 2026-07-26 | P007-ENC-P-01 P007-ENC-RR-01 P007-ENC-SSW-01 P007-ENC-USG-01 P007-ENC-USG-02 P007-TCR-NPE-01 P007-ENC-NMS-SW-01 P007-ENC-NMS-SW-03 P007-AAA-Server P007-eSight-Server P007-T-SOC-Server SOC-P003-P015 P007-SOC-RMC SOC_P012 SOC-TCC-P004 | Adel | Power Module Stopped Working | power alarm | planned activity of Tunnel electrical team |  | Zone 52 | 25.2942202° 51.4657002° | Outside Doha | P3 - Medium | 2026-07-26 20:22 | 2026-07-26 20:24 | 2 | 2026-07-26 20:22 | 2026-07-26 21:38 | 75.7167 | 75.7167 | planned activity by Tunnel electrical team | Completed | Non-maintainer | Planned Activity | Planned Activity | Alarm Cleared | -
654 | Sirti-WAN-R3-Ticket-617 | NA | 2026-07-26 | P007-ENC-NMS-SW-01 | Abubaker | Link Down | LAN Link Down | P007-ENC-NMS-SW-01, interface GE1/0/24, labelled “BATTERY-BANK for P007,” is down |  | Zone 52 | 25.2942202° 51.4657002° | Outside Doha | P3 - Medium | 2026-07-26 20:52 | 2026-07-26 20:57 | 4.5 | 2026-07-26 20:52 | 2026-07-26 21:07 | 14.5 | 14.5 | After a planned activity by Tunnel electrical team our team found that the 500 A ABB SACE Tmax battery breaker inside Battery Cabinet-A could not be restored to the normal ON position, Issue escalated to the concerned team | Completed | Non-maintainer | Planned Activity | N/A | Alarm Cleared | -
655 | Sirti-WAN-R3-Ticket-618 | NA | 2026-07-27 | P017C2-ENC23-CE-01.omc.local | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | No Power at the cabinet as the CB was tripped at the feeder pillar |  | Zone 57 | 25.1702778° 51.4710278° | Outside Doha | P2 - High | 2026-07-27 00:37 | 2026-07-27 00:40 | 3 | 2026-07-27 01:10 | 2026-07-27 01:30 | 19.8667 | 53.25 | The FLM team switched on the CB at the feeder pillar and found a damaged A/C cable causing a short circuit. The team repaired the A/C wiring, fixed the copper pipe leakage, replaced the faulty capacitor and refilled the refrigerant gas. | Completed | Non-maintainer | 3rd Party | KAHRAMAA | Device Restored | Rizwan
656 | Sirti-WAN-R3-Ticket-619 | NA | 2026-07-27 | P059C1-N3-ENC33-CE-01 | Adel | Link Down | LAN Link Down | kahromaa team is working at FP side |  | Zone 70 | 25.53313695° 51.41207372° | Outside Doha | P3 - Medium | 2026-07-27 15:50 | 2026-07-27 15:53 | 3 | 2026-07-27 17:31 | 2026-07-27 17:48 | 17.6333 | 118.6333 | kahromaa team is working at FP side | Completed | Non-maintainer | 3rd Party | KAHRAMAA | Alarm Cleared | Ahmed
657 | Sirti-WAN-R3-Ticket-620 | NA | 2026-07-27 | P011-ENC55-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | FLM is installing UPS on site |  | Zone 49 | 25.2209722° 51.5862222° | Outside Doha | P2 - High | 2026-07-27 22:26 | 2026-07-27 22:27 | 1 | 2026-07-27 22:26 | 2026-07-27 22:36 | 9.75 | 9.75 | FLM is installing UPS on site | Completed | Non-maintainer | Defect | UPS | Device Restored | Farouq
658 | Sirti-WAN-R3-Ticket-621 | NA | 2026-07-28 | P005-ENC412-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | During PPM, a loose connection found at the main CB for the Mains cable comming from the feeder pillar |  | Zone 51 | 25.3203266° 51.4472961° | Outside Doha | P2 - High | 2026-07-28 01:10 | 2026-07-28 01:11 | 1 | 2026-07-28 01:10 | 2026-07-28 01:15 | 4.8667 | 4.8667 | The FLM team switched off the main CB, reconnected the mains cable, and tightened the cable connection at the main CB. | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Rizwan
659 | Sirti-WAN-R3-Ticket-622 | NA | 2026-07-28 | P059C1-N3-ENC33-CE-01 | Adel | Link Down | LAN Link Down | LAN switch is hanged due ti high tem |  | Zone 70 | 25.53313695° 51.41207372° | Outside Doha | P3 - Medium | 2026-07-28 16:18 | 2026-07-28 16:20 | 2 | 2026-07-28 17:50 | 2026-07-28 18:04 | 13.65 | 105.75 | FLM restarted LAN switch | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | sanjeewa
660 | Sirti-WAN-R3-Ticket-623 | NA | 2026-07-28 | P060-ENC57-CE-GME-01.omc.local | Adel | Link Down | LAN Link Down | LAN Switch is faulty |  | Zone 69 | 25.4572929° 51.4787028° | Outside Doha | P3 - Medium | 2026-07-28 17:48 | 2026-07-28 17:50 | 2 | 2026-07-28 18:30 | 2026-07-28 20:42 | 132.2833 | 174.45 | FLM replaced LAN switch | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | sanjeewa
661 | Sirti-WAN-R3-Ticket-624 | NA | 2026-07-28 | P012-ENC30-NPE-01 | Adel | Link Down | WAN Link Down | Interface 100GE2/3/0/2 toward P017C1-ENC01-UPE-02 is down due to damaged patch cord at P017C1-ENC01-UPE-02 |  | Zone 56 | 25.2162349° 51.5021362° | Outside Doha | P3 - Medium | 2026-07-28 22:34 | 2026-07-28 22:36 | 2 | 2026-07-28 23:52 | 2026-07-29 00:38 | 45.8833 | 123.3 | Replaced the damaged patch cord at P017C1-ENC01-UPE-02 with a new patch cord | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Hassan
662 | Sirti-WAN-R3-Ticket-625 | NA | 2026-07-29 | SAL-ENC04-UPE-01 SAL-ENC04-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 57 | 25.2204517° 51.4230388° | Outside Doha | P2 - High | 2026-07-29 00:12 | 2026-07-29 00:15 | 2.65 | 2026-07-29 00:12 | 2026-07-29 00:32 | 19.5 | 19.5 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
663 | Sirti-WAN-R3-Ticket-626 | NA | 2026-07-29 | 22FEB-ENC25-UPE-02 22FEB-ENC25-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 43 | 25.31832397° 51.47088144° | Outside Doha | P2 - High | 2026-07-29 10:08 | 2026-07-29 10:11 | 3.0667 | 2026-07-29 10:08 | 2026-07-29 10:14 | 5.65 | 5.65 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
664 | Sirti-WAN-R3-Ticket-626 | NA | 2026-07-29 | DC23-ENC104-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 51 | 25.320812° 51.469483° | Outside Doha | P2 - High | 2026-07-29 10:08 | 2026-07-29 10:11 | 3.0667 | 2026-07-29 10:08 | 2026-07-29 10:14 | 5.65 | 5.65 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
665 | Sirti-WAN-R3-Ticket-627 | NA | 2026-07-29 | 22FEB-ENC25-UPE-02 22FEB-ENC25-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 43 | 25.31832397° 51.47088144° | Outside Doha | P2 - High | 2026-07-29 10:52 | 2026-07-29 10:54 | 2.5 | 2026-07-29 10:52 | 2026-07-29 10:57 | 5.6333 | 5.6333 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
666 | Sirti-WAN-R3-Ticket-627 | NA | 2026-07-29 | DC23-ENC104-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 51 | 25.320812° 51.469483° | Outside Doha | P2 - High | 2026-07-29 10:52 | 2026-07-29 10:54 | 2.5 | 2026-07-29 10:52 | 2026-07-29 10:57 | 5.6333 | 5.6333 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
667 | Sirti-WAN-R3-Ticket-628 | NA | 2026-07-29 | P060-ENC185-CE-DGME-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 74 | 25.65572° 51.49936° | Outside Doha | P2 - High | 2026-07-29 19:01 | 2026-07-29 19:06 | 5 | 2026-07-29 19:07 | 2026-07-29 19:08 | 1 | 7.1 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
668 | Sirti-WAN-R3-Ticket-629 | NA | 2026-07-29 | P060-ENC185-CE-DGME-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 74 | 25.65572° 51.49936° | Outside Doha | P2 - High | 2026-07-29 20:17 | 2026-07-29 20:19 | 2.1833 | 2026-07-29 20:20 | 2026-07-29 20:21 | 1.0667 | 4.75 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
669 | Sirti-WAN-R3-Ticket-630 | NA | 2026-07-29 | P028C2-ENC-01-CE-01.omc.local | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | A planned activity for connecting the UPS |  | Zone 70 | 25.2839108° 51.5496128° | Outside Doha | P2 - High | 2026-07-29 23:27 | 2026-07-29 23:27 | 0 | 2026-07-29 23:27 | 2026-07-29 23:38 | 10.8167 | 10.8167 | FLM team connected the UPS and batteries for supplying power to the cabinet and made the UPS operational | Completed | Non-maintainer | Planned Activity | UPS | Device Restored | Rizwan
670 | Sirti-WAN-R3-Ticket-631 | NA | 2026-07-29 | P028C2-ENC-01-CE-01.omc.local | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | A planned activity to test the UPS and battery functionality |  | Zone 70 | 25.2839108° 51.5496128° | Outside Doha | P2 - High | 2026-07-29 23:47 | 2026-07-29 23:47 | 0 | 2026-07-29 23:47 | 2026-07-29 23:52 | 5.1667 | 5.1667 | FLM team tested the functionality of the UPS and checked the batteries health | Completed | Non-maintainer | Planned Activity | UPS | Device Restored | Rizwan
671 | Sirti-WAN-R3-Ticket-632 | NA | 2026-07-30 | P007C7P2-ENC15-CE-01 P007C7P2-ENC15-UPE-01 P007C7P2-ENC048-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | No Power at the cabinet as the CB was tripped at the feeder pillar |  | Zone 51 | 25.3206257° 51.4593901° | Outside Doha | P2 - High | 2026-07-30 01:21 | 2026-07-30 01:24 | 3.45 | 2026-07-30 01:54 | 2026-07-30 02:29 | 34.6333 | 68.4333 | The FLM team switched ON the tripped CB at the feeder pillar and restored the devices | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Hassan
672 | Sirti-WAN-R3-Ticket-633 | NA | 2026-07-30 | 22FEB-ENC25-UPE-02 22FEB-ENC25-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 43 | 25.31832397° 51.47088144° | Outside Doha | P2 - High | 2026-07-30 09:28 | 2026-07-30 09:30 | 2.5833 | 2026-07-30 09:28 | 2026-07-30 09:36 | 8.15 | 8.15 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
673 | Sirti-WAN-R3-Ticket-633 | NA | 2026-07-30 | DC23-ENC104-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | kahromaa power interruption |  | Zone 51 | 25.320812° 51.469483° | Outside Doha | P2 - High | 2026-07-30 09:28 | 2026-07-30 09:30 | 2.5833 | 2026-07-30 09:28 | 2026-07-30 09:36 | 8.15 | 8.15 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
674 | Sirti-WAN-R3-Ticket-634 | NA | 2026-07-30 | P004-ENC43-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | Alarm Auto cleared before FLM reach the site |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-07-30 13:53 | 2026-07-30 13:56 | 2.2667 | 2026-07-30 15:07 | 2026-07-30 15:08 | 1.0833 | 75.0667 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
675 | Sirti-WAN-R3-Ticket-635 | NA | 2026-07-30 | P023C2-ENC43-CE-01 | Aaqib | Link Down | LAN LinkPort XGE 0/0/4 (ENC-43-USW-4) down | Alarm Auto cleared before FLM reach the site |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-07-30 13:39 | 2026-07-30 13:41 | 2.1 | 2026-07-30 15:33 | 2026-07-30 15:35 | 1.1833 | 115.5167 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
676 | Sirti-WAN-R3-Ticket-636 | NA | 2026-07-31 | P059C1-N3-ENC33-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | KAHRAMAA power interruption |  | Zone 79 | 26.11086393 51.228551 | Outside Doha | P2 - High | 2026-07-31 05:17 | 2026-07-31 05:28 | 11.3 | 2026-07-31 05:17 | 2026-07-31 06:01 | 44.4833 | 44.4833 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
677 | Sirti-WAN-R3-Ticket-637 | NA | 2026-07-31 | P004-ENC43-UPE-02 | Sanket | Temperature higher than Upper threshold | High Temperature | AC not working |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-07-31 13:48 | 2026-07-31 13:53 | 5.05 | 2026-07-31 15:22 | 2026-07-31 15:31 | 9.55 | 103.6333 | A faulty sensor was identified in the A/C unit, and the refrigerant (R22A) level was found to be below the required operating level, resulting in reduced cooling performance. The FLM team replaced the faulty sensor, recharged the system with R22A refrigerant to the specified level, and verified that the A/C unit was operating normally with the required cooling performance. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | patrick
678 | Sirti-WAN-R3-Ticket-638 | NA | 2026-07-31 | P023C2-ENC43-CE-01 | Sanket | Link Down | LAN LinkPort XGE 0/0/4 (ENC-43-USW-4) down | AMG Switch hanged due to high temperature |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-07-31 13:50 | 2026-07-31 13:53 | 2.8667 | 2026-07-31 15:22 | 2026-07-31 15:28 | 5.9 | 97.8 | AMG LAN Switch was hanged due to high temperature inside cabinet | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | patrick
679 | Sirti-WAN-R3-Ticket-639 | NA | 2026-07-31 | P008C2-ENC37-UPE-02 | Sanket | Temperature higher than Upper threshold | High Temperature | AC not cooling |  | Zone 56 | 25.223739° 51.532902° | Outside Doha | P3 - Medium | 2026-07-31 14:20 | 2026-07-31 14:24 | 3.3667 | 2026-07-31 16:50 | 2026-07-31 17:02 | 11.4667 | 161.5167 | AC not working. Alarm clear after opening door by FLM | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | patrick
680 | Sirti-WAN-R3-Ticket-640 | NA | 2026-08-01 | P007C7P2-ENC15-CE-01 P007C7P2-ENC15-UPE-01 P007C7P2-ENC048-CE-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | No Power at the cabinet as the CB was tripped at the feeder pillar |  | Zone 51 | 25.3206257° 51.4593901° | Outside Doha | P2 - High | 2026-08-01 06:13 | 2026-08-01 06:25 | 12.3667 | 2026-08-01 08:21 | 2026-08-01 08:44 | 23.6333 | 151.5667 | The FLM team switched ON the tripped CB at the feeder pillar and restored the devices | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Eric
681 | Sirti-WAN-R3-Ticket-641 | NA | 2026-08-01 | P007C2-ENC01-UPE-01 | Sanket | Temperature higher than Upper threshold | High Temperature | Alarm Auto cleared before FLM reach the site |  | Zone 38 | 25.2931613° 51.4894255° | Inside Doha | P3 - Medium | 2026-08-01 11:59 | 2026-08-01 12:06 | 7 | 2026-08-01 13:12 | 2026-08-01 13:14 | 2 | 75 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
682 | Sirti-WAN-R3-Ticket-642 | NA | 2026-08-01 | P004-ENC67-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 80 | 25.3632065° 51.2505727° | Outside Doha | P2 - High | 2026-08-01 12:25 | 2026-08-01 12:31 | 5.4333 | 2026-08-01 14:30 | 2026-08-01 14:31 | 1 | 125.5667 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored
683 | Sirti-WAN-R3-Ticket-643 | NA | 2026-08-01 | P010-ENC01-UPE-01 | Sanket | Temperature higher than Upper threshold | High Temperature | AC not cooling |  | Zone 81 | 25.1398815° 51.4073931° | Outside Doha | P3 - Medium | 2026-08-01 12:50 | 2026-08-01 13:02 | 12.15 | 2026-08-01 12:50 | 2026-08-01 13:43 | 53.0667 | 53.0667 | AC was running but not cooling properly. Operating parameters were adjusted, restoring normal cooling. Cabinet temperature is now normal for now and under observation | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
684 | Sirti-WAN-R3-Ticket-644 | NA | 2026-08-01 | P007C5P1-ENC25-CE-01 | Sanket | Link Down | LAN Link Down | Link GI 1/13 down towards LAN. LAN switch was handed due to high temeprature |  | Zone 54 | 25.286628° 51.466131° | Outside Doha | P3 - Medium | 2026-08-01 13:29 | 2026-08-01 13:38 | 9.4167 | 2026-08-01 15:51 | 2026-08-01 16:07 | 15.75 | 158.1667 | LAN switch hung due to high cabinet temperature. Rebooted by FLM. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Ghulam
685 | Sirti-WAN-R3-Ticket-645 | NA | 2026-08-01 | P023C2-ENC16-CE-01 | Sanket | Link Down | LAN Link Down | Link XGE 0/0/4 down towards LAN |  | Zone 82 | 25.228079° 51.307359° | Outside Doha | P3 - Medium | 2026-08-01 13:50 | 2026-08-01 14:00 | 9.7667 | 2026-08-01 13:50 | 2026-08-01 14:47 | 56.4667 | 56.4667 | LAN device auto-restored, and the connected switch port also restored | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
686 | Sirti-WAN-R3-Ticket-646 | NA | 2026-08-01 | P007C5P1-ENC25-CE-01 | Aaqib | Link Down | LAN Link Down | Link GI 1/13 down towards LAN. LAN switch is hanging |  | Zone 54 | 25.286628° 51.466131° | Outside Doha | P3 - Medium | 2026-08-01 21:33 | 2026-08-01 21:48 | 15.0667 | 2026-08-01 22:55 | 2026-08-01 23:13 | 17.4833 | 100.1667 | FLM replaced faulty LAN switch | Completed | Non-maintainer | No Node Down | LAN SW replaced | Alarm Cleared | Rizwan
687 | Sirti-WAN-R3-Ticket-647 | NA | 2026-08-01 | P007C5P1-ENC25-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device down during troubleshooting AC issue |  | Zone 54 | 25.286628° 51.466131° | Outside Doha | P2 - High | 2026-08-01 21:37 | 2026-08-01 21:44 | 6.9167 | 2026-08-01 21:37 | 2026-08-01 21:43 | 5.2667 | 5.2667 | Device down during troubleshooting AC issue | Completed | Non-maintainer | Defect | AC | Device Restored | Ghulam
688 | Sirti-WAN-R3-Ticket-648 | NA | 2026-08-01 | COR-ENC12-CE-01 | Abubaker | Link Down | LAN Link Down | XGigabitEthernet 0/1/7 toward LAN switch SW1/R1-ENC02 is down |  | Zone 61 | 25.324005699251956 51.52792742883553 | Outside Doha | P3 - Medium | 2026-08-01 23:34 | 2026-08-01 23:41 | 7.45 | 2026-08-02 00:34 | 2026-08-02 01:25 | 51.0333 | 111.1333 | LAN switch was down due to tripped CB, FLM team switched ON the CB and made the LAN device operational and alarm cleared | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | Rizwan
689 | Sirti-WAN-R3-Ticket-649 | NA | 2026-08-01 | P007C2-170018-R2-CSW | Abubaker | Link Down | LAN Link Down | Interface GE 2/0/16 toward LAN device is down |  | Zone 52 | 25.2942202 51.4657002 | Outside Doha | P3 - Medium | 2026-08-01 23:52 | 2026-08-02 00:04 | 11.6167 | 2026-08-01 23:52 | 2026-08-02 00:14 | 21.25 | 21.25 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | -
690 | Sirti-WAN-R3-Ticket-650 | NA | 2026-08-02 | P007C2-ENC01-UPE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC is not cooling |  | Zone 38 | 25.2931613° 51.4894255° | Inside Doha | P3 - Medium | 2026-08-02 11:59 | 2026-08-02 12:05 | 5.5833 | 2026-08-02 14:20 | 2026-08-02 14:25 | 5 | 146.5333 | FLM Cleaned AC filter & AC unit and filled gas | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
691 | Sirti-WAN-R3-Ticket-651 | NA | 2026-08-02 | P008C2-ENC37-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC is not cooling properly |  | Zone 56 | 25.223739° 51.532902° | Outside Doha | P3 - Medium | 2026-08-02 13:14 | 2026-08-02 13:16 | 2.3833 | 2026-08-02 14:20 | 2026-08-02 14:31 | 11 | 77.25 | FLM Cleaned AC filter & AC condenser | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Ghulam
692 | Sirti-WAN-R3-Ticket-652 | NA | 2026-08-02 | P002-ENC07-UPE-01 | Aaqib | Temperature higher than Upper threshold | High Temperature | The AC unit was operational, but its cooling performance was below normal due to a clogged condenser fan filter caused by dust buildup. |  | Zone 55 | 25.257° 51.486° | Outside Doha | P3 - Medium | 2026-08-02 14:21 | 2026-08-02 14:24 | 3.2167 | 2026-08-02 14:31 | 2026-08-02 14:37 | 6 | 15.75 | The condenser fan filter was cleaned with water, the UP filter was cleaned using a blower, and the thermostat settings were adjusted. The unit was tested, and normal cooling performance was successfully restored. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Eric
693 | Sirti-WAN-R3-Ticket-653 | NA | 2026-08-02 | P023C2-ENC43-CE-01 | Adel | Link Down | LAN LinkPort XGE 0/0/4 (ENC-43-USW-4) down | AMG Switch hanged due to high temperature |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-08-02 14:43 | 2026-08-02 14:45 | 2 | 2026-08-02 15:30 | 2026-08-02 15:49 | 19.0167 | 66.1 | FLM restarted LAN AMG Switch | Completed | Non-maintainer | No Node Down | LAN SW restarted | Alarm Cleared | -
694 | Sirti-WAN-R3-Ticket-654 | NA | 2026-08-03 | P010-ENC89-UPE-02 | Aaqib | CPU temperature too High | High Temperature | AC is not cooling |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | P3 - Medium | 2026-08-03 09:10 | 2026-08-03 09:18 | 7.6 | 2026-08-03 19:21 | 2026-08-03 19:40 | 19 | 629.5 | Visited site, checked power and voltage, repaired leaking compressor capillary pipe, cleaned and vacuumed the system, recharged with R22 gas, serviced the AC | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
695 | Sirti-WAN-R3-Ticket-655 | NA | 2026-08-03 | P008C2-Enc18-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | no kahromaa power inside WAN cabinet |  | Zone 56 | 25.2344284° 51.5198792° | Outside Doha | P2 - High | 2026-08-03 13:39 | 2026-08-03 13:43 | 3.5333 | 2026-08-03 15:40 | 2026-08-03 16:41 | 61.4333 | 182.2667 | FLM raise a compain to kahromaa , power retored after kahromaa team solve the issue. reference No for KAHRAMAA 261100040417 | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | Khadar
696 | Sirti-WAN-R3-Ticket-656 | NA | 2026-08-03 | P006-ENC17-UPE02 P006-ENC17-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | planned activity to install UPS inside cabinet |  | Zone 56 | 25.19614, 51.45325 | Outside Doha | P2 - High | 2026-08-03 21:36 | 2026-08-03 21:38 | 2 | 2026-08-03 21:36 | 2026-08-03 22:00 | 24.4167 | 24.4167 | planned activity to install UPS inside cabinet | Completed | Non-maintainer | Planned Activity | UPS | Alarm Cleared | Ghulam
697 | Sirti-WAN-R3-Ticket-657 | NA | 2026-08-04 | SAL-ENC09-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-08-04 02:43 | 2026-08-04 02:44 | 1.0167 | 2026-08-04 02:44 | 2026-08-04 02:45 | 0.93333 | 1.9833 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
698 | Sirti-WAN-R3-Ticket-658 | NA | 2026-08-04 | P023C1-ENC05-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 92 | 25.0293756° 51.5193707° | Outside Doha | P2 - High | 2026-08-04 02:52 | 2026-08-04 02:53 | 1.05 | 2026-08-04 02:55 | 2026-08-04 02:56 | 0.96667 | 3.95 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
699 | Sirti-WAN-R3-Ticket-659 | NA | 2026-08-04 | P023C1-ENC01-CE-01 | Arif | Link Down | LAN Link Down | Interface TE 1/28 toward DIST 7 (LAN) device |  | Zone 90 | 25.111748° 51.583897° | Outside Doha | P3 - Medium | 2026-08-04 02:51 | 2026-08-04 02:56 | 4.6167 | 2026-08-04 03:38 | 2026-08-04 03:39 | 1 | 47.6 | The link is down towards LAN and Autorestored. | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | -
700 | Sirti-WAN-R3-Ticket-660 | NA | 2026-08-04 | P029C1-ENC01-CE-01.omc.local | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | The CB tripped |  | Zone 53 | 25.2721112° 51.4331388° | Outside Doha | P2 - High | 2026-08-04 06:17 | 2026-08-04 06:24 | 7.0167 | 2026-08-04 07:04 | 2026-08-04 07:22 | 18.0667 | 64.6 | The main circuit breaker tripped. Reset the main breaker to restore power. Visited the site, repaired the leaking compressor pipe, cleaned and leak-tested the system, vacuumed and refilled R22A gas, serviced the AC, and confirmed it is now cooling properly without tripping the breaker. | Completed | Non-maintainer | Defect | AC | Device Restored | Umair/Khader
701 | Sirti-WAN-R3-Ticket-661 | NA | 2026-08-04 | P029C1-ENC01-CE-01.omc.local | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 53 | 25.2721112° 51.4331388° | Outside Doha | P2 - High | 2026-08-04 08:34 | 2026-08-04 08:36 | 1.35 | 2026-08-04 08:38 | 2026-08-04 08:40 | 1.9 | 5.25 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
702 | Sirti-WAN-R3-Ticket-662 | NA | 2026-08-04 | P010-ENC61-CE-01 | Amr | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 57 | 25.1700975° 51.4699752° | Outside Doha | P2 - High | 2026-08-04 15:31 | 2026-08-04 15:35 | 4 | 2026-08-04 15:36 | 2026-08-04 15:47 | 10.9167 | 16.35 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
703 | Sirti-WAN-R3-Ticket-663 | NA | 2026-08-04 | P040-CPE02-ENC21-DSW | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 57 | 25.189354° 51.448508° | Outside Doha | P2 - High | 2026-08-04 18:48 | 2026-08-04 18:49 | 1 | 2026-08-04 18:48 | 2026-08-04 18:55 | 7.1667 | 7.1667 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
704 | Sirti-WAN-R3-Ticket-664 | NA | 2026-08-05 | P007C1-ENC31-UPE-01 | Sanket | Link Down | WAN Link Down | 100G link down at P007C1-ENC31-UPE-01 100GE 1/0/4 towards P007C1-ENC02-UPE02 100GE 1/0/4 |  | Zone 52 | 25.298365 51.437959 | Outside Doha | P3 - Medium | 2026-08-05 12:27 | 2026-08-05 12:33 | 5.5 | 2026-08-05 15:30 | 2026-08-05 19:28 | 238.4 | 421.15 | FLM replaced patchcord at ENC31 side , alarm is clear and optical values are in range | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Ahmed
705 | Sirti-WAN-R3-Ticket-665 | NA | 2026-08-05 | P028C2-ENC06-DGME-CE-01 | Sanket | Link Down | LAN Link Down | 1G link down at P028C2-ENC06-DGME-01 port Gi 1/2 towards AR-ENC06-USW-02 |  | Zone 13 | 25.2892675° 51.5213447° | Inside Doha | P3 - Medium | 2026-08-05 14:15 | 2026-08-05 14:19 | 4.0333 | 2026-08-05 15:30 | 2026-08-05 17:19 | 108.7 | 183.75 | FLM restarted Hanged LAN switch due to overheat | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Irshad
706 | Sirti-WAN-R3-Ticket-666 | NA | 2026-08-05 | P059C1-N3-ENC20-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Egis team is doing activity on site |  | Zone 70 | 25.44194931° 51.41112813° | Outside Doha | P2 - High | 2026-08-05 15:33 | 2026-08-05 15:38 | 5 | 2026-08-05 16:27 | 2026-08-05 17:20 | 53.2833 | 107.1167 | Egis company was working on FP. After the maintenance they restored the power | Completed | Non-maintainer | 3rd Party | Egis | Device Restored | Najeeb
707 | Sirti-WAN-R3-Ticket-667 | NA | 2026-08-05 | P004-MOQ-CE-01 | Adel | Link Down | LAN Link Down | QNBN Team disconnected the link |  | Zone 51 | 25.319385° 51.352255° | Outside Doha | P3 - Medium | 2026-08-05 16:48 | 2026-08-05 16:51 | 3 | 2026-08-05 16:56 | 2026-08-05 17:00 | 4.35 | 12.35 | QNBN Team has decommissioned the link as requested by PWA Edward | Completed | Non-maintainer | 3rd Party | QNBN , decommissioning | Alarm Active | Hassan/khadar
708 | Sirti-WAN-R3-Ticket-668 | NA | 2026-08-05 | P042-ENC08-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 49 | 25.226270° 51.590859° | Outside Doha | P2 - High | 2026-08-05 21:42 | 2026-08-05 21:44 | 2 | 2026-08-05 21:42 | 2026-08-05 21:47 | 5.6333 | 5.6333 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
709 | Sirti-WAN-R3-Ticket-669 | NA | 2026-08-05 | P042-ENC01-CE-01 P042-ENC08-CE-01.omc.local | Adel | Link Down | LAN Link Down | port 1/15 towards RBF uplink , QNBN Team disconnected the link |  | Zone 49 | 25.226270° 51.590859° | Outside Doha | P3 - Medium | 2026-08-05 17:37 | 2026-08-05 17:38 | 1 | 2026-08-05 17:45 | 2026-08-05 17:52 | 7 | 15 | QNBN Team has decommissioned the link as requested by PWA Edward | Completed | Non-maintainer | 3rd Party | QNBN , decommissioning | Alarm Active
710 | Sirti-WAN-R3-Ticket-670 | NA | 2026-08-06 | DC23-ENC102-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | The Main CB tripped |  | Zone 32 | 25.321261° 51.473693° | Inside Doha | P2 - High | 2026-08-06 00:28 | 2026-08-06 00:34 | 6 | 2026-08-06 00:59 | 2026-08-06 01:07 | 8.3167 | 39.1333 | The main circuit breaker tripped. Reset the main breaker to restore power. Installed and connected all required AC components, including compressor, motors, wiring, valves, filter drier, copper pipes, capacitors, thermostat, sensor, and gas charging valve. | Completed | Non-maintainer | Defect | AC | Device Restored | Hassan/Rizwan
711 | Sirti-WAN-R3-Ticket-671 | NA | 2026-08-06 | IE5000-1702.ashghal | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | CB Tripped during PPM |  | Zone 18 | 25.2833249904° 51.551376977 | Inside Doha | P2 - High | 2026-08-06 03:56 | 2026-08-06 03:58 | 2 | 2026-08-06 04:07 | 2026-08-06 04:15 | 7.3167 | 18.15 | Device went down due to ongoing PPM activity by FLM | Completed | Non-maintainer | Planned Activity | PPM | Network Back Online | Suhail
712 | Sirti-WAN-R3-Ticket-672 | NA | 2026-08-06 | P029C1-ENC01-CE-01.omc.local | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Main CB is tripped due to AC compressor short circuit |  | Zone 53 | 25.2721112° 51.4331388° | Outside Doha | P2 - High | 2026-08-06 12:41 | 2026-08-06 12:45 | 3.3667 | 2026-08-06 15:40 | 2026-08-06 16:32 | 52.1833 | 230.9667 | FLM switched off AC on cabinet to restore the CE node , AC team visited the site and confirmed AC compressor is faulty and need replacement , pending spares parts | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Ahmed
713 | Sirti-WAN-R3-Ticket-673 | NA | 2026-08-06 | P004-ENC43-UPE-02 P023C2-ENC43-CE-01 | Sanket | Temperature higher than Upper threshold | High Temperature / LAN Link Down | AC Compressor Faulty |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-08-06 13:40 | 2026-08-06 13:52 | 12.8833 | 2026-08-06 15:30 | 2026-08-06 16:09 | 38.7 | 149.1667 | The faulty AC compressor was replaced, the refrigeration system was serviced, and the unit was tested and confirmed to be operating normally with the cabinet temperature restored to normal | Completed | Non-maintainer | Defect | AC | Device Restored | Ghulam
714 | Sirti-WAN-R3-Ticket-674 | NA | 2026-08-06 | P008C3-ENC25-UPE-02 | Sanket | Temperature higher than Upper threshold | High Temperature | AC is not cooling properly |  | Zone 56 | 25.2341068° 51.50261 | Outside Doha | P3 - Medium | 2026-08-06 14:14 | 2026-08-06 14:23 | 9.1833 | 2026-08-06 14:30 | 2026-08-06 14:38 | 8.3333 | 24.3333 | Visited site, checked power and voltage, repaired leaking compressor capillary pipe, cleaned and vacuumed the system, recharged with R22 gas, serviced the AC | Completed | Non-maintainer | Defect | AC | Device Restored | Rizwan
715 | Sirti-WAN-R3-Ticket-675 | NA | 2026-08-06 | P002-ENC14-UPE-02 | Sanket | Temperature higher than Upper threshold | High Temperature | The temperature autorestore |  | Zone 55 | 25.249° 51.471° | Outside Doha | P3 - Medium | 2026-08-06 13:56 | 2026-08-06 14:05 | 9.3667 | 2026-08-06 14:42 | 2026-08-06 14:43 | 1.0167 | 47.3167 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
716 | Sirti-WAN-R3-Ticket-676 | NA | 2026-08-06 | P029C1-ENC01-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 53 | 25.2721112° 51.4331388° | Outside Doha | P2 - High | 2026-08-06 17:23 | 2026-08-06 17:24 | 1 | 2026-08-06 17:23 | 2026-08-06 17:28 | 4.9167 | 4.9167 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
| Sirti-WAN-R3-Ticket-677 | NA | 2026-08-06 | P004-ENC43-CE-01 P004-ENC43-UPE-02 P023C2-ENC43-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 82 | 25.1701761 51.3230788 | Outside Doha | P2 - High | 2026-08-06 20:59 | 2026-08-06 21:01 | 2 | 2026-08-06 20:59 | 2026-08-06 21:05 | 5.8333 | 5.8333 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
718 | Sirti-WAN-R3-Ticket-678 | NA | 2026-08-07 | P007C5P1-ENC26-CE-01.omc.local | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | CB Tripped at ITS FP side |  | Zone 55 | 25.2663028° 51.4683846° | Outside Doha | P2 - High | 2026-08-07 13:11 | 2026-08-07 13:15 | 4.1333 | 2026-08-07 15:56 | 2026-08-07 16:24 | 28.1167 | 192.8333 | Main CB at ITS FP was tripped. Devices restored after turning CB ON | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Ahmed
719 | Sirti-WAN-R3-Ticket-679 | NA | 2026-08-07 | P023C1-ENC16-CE-01 | Sanket | Link Down | LAN Link Down | The 10G link towards USW XG 0/0/4 is down |  | Zone 82 | 25.228079° 51.307359° | Outside Doha | P3 - Medium | 2026-08-07 13:41 | 2026-08-07 13:53 | 12 | 2026-08-07 14:36 | 2026-08-07 14:37 | 1.0667 | 55.9 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
720 | Sirti-WAN-R3-Ticket-680 | NA | 2026-08-07 | P004-ENC35-UPE-01 | Sanket | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 53 | 25.3298055° 51.3348478° | Outside Doha | P3 - Medium | 2026-08-06 13:58 | 2026-08-06 14:03 | 5.1167 | 2026-08-07 22:51 | 2026-08-08 02:45 | 234.5167 | 2207.2833 | Visiteed site,The AC unit was dismantled, inspected, thoroughly cleaned, vacuumed, recharged with refrigerant, reassembled, and tested, after which it was found operating normally with stable and efficient cooling performance. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan
721 | Sirti-WAN-R3-Ticket-681 | NA | 2026-08-07 | SAL-ENC26-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 81 | 25.1435454° 51.2478413° | Outside Doha | P2 - High | 2026-08-07 14:10 | 2026-08-07 14:14 | 3.15 | 2026-08-07 14:10 | 2026-08-07 15:08 | 57.5 | 57.5 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
722 | Sirti-WAN-R3-Ticket-682 | NA | 2026-08-07 | SAL-ENC20-CE-01 SAL-ENC20-UPE-02 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | P2 - High | 2026-08-07 15:04 | 2026-08-07 15:05 | 1 | 2026-08-07 15:04 | 2026-08-07 15:08 | 3.5 | 3.5 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
723 | Sirti-WAN-R3-Ticket-683 | NA | 2026-08-07 | P061-ENC11-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 54 | 25.276554° 51.473967° | Outside Doha | P2 - High | 2026-08-07 15:59 | 2026-08-07 16:00 | 0.7 | 2026-08-07 15:59 | 2026-08-07 16:05 | 5.8 | 5.8 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
724 | Sirti-WAN-R3-Ticket-684 | NA | 2026-08-07 | P015-ENC80A-CE-01 | Arif | Link Heartbeat Packet Loss Reaching | LAN Link Down | GE1/0/4 Link towards LAN Access Ring-4 is down |  | Zone 90 | 25.113315° 51.5735937° | Outside Doha | P3 - Medium | 2026-08-07 23:54 | 2026-08-07 23:55 | 1.1667 | 2026-08-07 23:54 | 2026-08-07 23:58 | 3.9333 | 3.9333 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | -
725 | Sirti-WAN-R3-Ticket-685 | NA | 2026-08-08 | P059C1-N2-ENC19-CE-01 | Arif | Link Down | LAN Link Down | Port XG 0/0/3 towards shamal-N2-ENC-33 |  | Zone 70 | 25.43425476° 51.412436° | Outside Doha | P3 - Medium | 2026-08-08 06:28 | 2026-08-08 06:36 | 8 | 2026-08-08 07:20 | 2026-08-08 07:57 | 36.5667 | 88.9667 | QBC egis power team working at street lights FP. | Completed | Non-maintainer | 3rd Party | Egis | Device Restored | Hichem
726 | Sirti-WAN-R3-Ticket-686 | NA | 2026-08-09 | P060-ENC185-CE-DGME-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 74 | 25.655612° 51.499318° | Outside Doha | P2 - High | 2026-08-09 02:25 | 2026-08-09 02:28 | 3 | 2026-08-09 02:28 | 2026-08-09 02:30 | 2 | 5 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
727 | Sirti-WAN-R3-Ticket-687 | NA | 2026-08-09 | P059C1-N3-ENC33-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 70 | 25.53313695° 51.41207372° | Outside Doha | P2 - High | 2026-08-09 09:31 | 2026-08-09 09:33 | 2 | 2026-08-09 09:33 | 2026-08-09 09:43 | 10 | 12 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
728 | Sirti-WAN-R3-Ticket-688 | NA | 2026-08-09 | P060-ENC38-CE-GME-03.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kahromaa shutdown activity |  | Zone 69 | 25.4301975 51.4851901° | Outside Doha | P2 - High | 2026-08-09 07:13 | 2026-08-09 07:15 | 2 | 2026-08-09 08:00 | 2026-08-09 08:48 | 48 | 95 | FLM Connnected PG till kahromaa power restored | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Umair
729 | Sirti-WAN-R3-Ticket-689 | NA | 2026-08-09 | P060-ENC38-CE-GME-04.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kahromaa shutdown activity |  | Zone 69 | 25.4311454° 51.4832727° | Outside Doha | P2 - High | 2026-08-09 07:13 | 2026-08-09 07:15 | 2 | 2026-08-09 08:00 | 2026-08-09 08:51 | 51 | 98 | FLM Connnected PG till kahromaa power restored | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Umair
730 | Sirti-WAN-R3-Ticket-690 | NA | 2026-08-09 | P060-ENC38-CE-GME-04.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | ITS FP MCB breaker tripped off |  | Zone 69 | 25.4311454° 51.4832727° | Outside Doha | P2 - High | 2026-08-09 10:13 | 2026-08-09 10:15 | 2 | 2026-08-09 16:21 | 2026-08-09 16:40 | 19 | 387 | Main CB at ITS FP was tripped. Devices restored after turning CB ON | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Khedar
731 | Sirti-WAN-R3-Ticket-691 | NA | 2026-08-10 | P002-ENC14-UPE-02 | Adel | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 55 | 25.249° 51.471° | Outside Doha | P3 - Medium | 2026-08-10 11:24 | 2026-08-10 11:26 | 2 | 2026-08-10 16:38 | 2026-08-10 21:32 | 294 | 608 | The AC unit was removed from the cabinet for inspection. It was found that the compressor had overheated due to a blockage in the dryer filter and capillary tube. The faulty dryer filter and capillary tube were replaced. After the repair, the AC was tested and confirmed to be working normally with proper cooling. The site is currently operating normally with no active alarms. The site will be monitored for the next 24 hours to ensure the cabinet temperature remains within the normal range and the AC continues to perform properly. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Ghulam
732 | Sirti-WAN-R3-Ticket-692 | NA | 2026-08-10 | P007C2-ENC01-UPE-01 | Adel | Temperature higher than Upper threshold | High Temperature | Found the AC filters and condenser were dusty and blocked |  | Zone 38 | 25.2931613° 51.4894255° | Inside Doha | P3 - Medium | 2026-08-10 13:05 | 2026-08-10 13:07 | 2 | 2026-08-10 20:16 | 2026-08-10 21:32 | 76 | 507 | FLM Team Cleaned the AC filters and AC unit using a blower and cloth towels. Also cleaned the AC parts and performed water servicing. Checked the gas level and all other components. The AC is now cooling properly and working normally. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khedar
733 | Sirti-WAN-R3-Ticket-693 | NA | 2026-08-10 | P028C2-ENC06-DGME-CE-01.omc.local | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 13 | 25.2892675° 51.5213447° | Inside Doha | P2 - High | 2026-08-10 22:11 | 2026-08-10 22:12 | 1 | 2026-08-10 22:12 | 2026-08-10 22:17 | 5 | 6 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
734 | Sirti-WAN-R3-Ticket-694 | NA | 2026-08-10 | P023C1-ENC01-CE-01 | Arif | Link Down | Interface TE 1/28 toward DIST 6 (LAN) device | CB was tripped for LAN cabinet |  | Zone 90 | 25.111748° 51.583897° | Outside Doha | P3 - Medium | 2026-08-10 23:22 | 2026-08-10 23:27 | 4.5667 | 2026-08-10 23:53 | 2026-08-11 00:08 | 15.5167 | 45.6833 | FLM Switched on tripped CB inside LAN cabinet | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Rizwan
735 | Sirti-WAN-R3-Ticket-695 | NA | 2026-08-11 | SAL-ENC04-UPE-01 SAL-ENC04-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Devices are Down | The Main Fedder Piller CB tripped |  | Zone 57 | 25.2204517° 51.4230388° | Outside Doha | P2 - High | 2026-08-11 05:54 | 2026-08-11 05:56 | 2.3333 | 2026-08-11 06:02 | 2026-08-11 06:36 | 34.55 | 42.4833 | The FLM team switched ON the tripped CB at the feeder pillar and restored the devices | Completed | Maintainer | N/A | N/A | Device Restored | Suhail
736 | Sirti-WAN-R3-Ticket-696 | NA | 2026-08-11 | P007C2-ENC99-UPE-02 | Adel | CPU temperature too High | High Temperature | the team identified that the AC condenser filter was blocked |  | Zone 52 | 25.2967109° 51.4488814° | Outside Doha | P3 - Medium | 2026-08-11 11:54 | 2026-08-11 11:56 | 2 | 2026-08-11 16:44 | 2026-08-11 18:30 | 106 | 395.85 | The team cleaned the condenser filter and properly refitted it. Following the cleaning, the AC is operating normally and providing adequate cooling. The high-temperature alarm has been cleared, and the site is now operating normally. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Ghulam
737 | Sirti-WAN-R3-Ticket-697 | NA | 2026-08-11 | P001-ENC01-UPE-01 | AMR | Temperature higher than Upper threshold | High Temperature | Found the AC filters and condenser were dusty and blocked |  | Zone 56 | 25.220542° 51.5173492° | Outside Doha | P3 - Medium | 2026-08-11 16:11 | 2026-08-11 16:13 | 2 | 2026-08-11 17:55 | 2026-08-11 21:32 | 217 | 321.25 | FLM Team Cleaned the AC filters and AC unit using a blower and cloth towels. Also cleaned the AC parts and performed water servicing. Checked the gas level and all other components. The AC is now cooling properly and working normally. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
738 | Sirti-WAN-R3-Ticket-698 | NA | 2026-08-11 | P028C2-ENC06-DGME-CE-01.omc.local | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | the main circuit breaker was tripped |  | Zone 13 | 25.2892675° 51.5213447° | Inside Doha | P2 - High | 2026-08-11 17:27 | 2026-08-11 17:29 | 2 | 2026-08-11 18:26 | 2026-08-11 18:32 | 5.5333 | 64.2667 | The FLM team switched ON the tripped CB at the ITS cabinet and restored the devices | Completed | Maintainer | N/A | N/A | Device Restored | Najeeb
739 | Sirti-WAN-R3-Ticket-699 | NA | 2026-08-11 | P001-ENC01-UPE-01 P001-ENC01-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | The CB tripped during AC troubleshooting activities |  | Zone 56 | 25.220542° 51.5173492° | Outside Doha | P2 - High | 2026-08-11 19:34 | 2026-08-11 19:35 | 1 | 2026-08-11 19:34 | 2026-08-11 19:42 | 8.3333 | 8.3333 | The FLM team switched ON the tripped CB and restored the devices | Completed | Non-maintainer | Defect | AC | Device Restored | Khadar
740 | Sirti-WAN-R3-Ticket-700 | NA | 2026-08-12 | P012-ENC101-CE-01 | Sanket | Link down | LAN link down | Interface TE 1/27 toward QA001 LAN device is down |  | Zone 57 | 25.1957136° 51.4525682° | Outside Doha | P3 - Medium | 2026-08-12 06:16 | 2026-08-12 06:17 | 1.1667 | 2026-08-12 06:17 | 2026-08-12 06:19 | 1.1 | 2.3167 | The link is down towards LAN and Autorestored. | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | -
741 | Sirti-WAN-R3-Ticket-701 | NA | 2026-08-12 | P059C1-N2-ENC19-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | QBC Team are doing activity at the FP |  | Zone 70 | 25.43425476° 51.412436° | Outside Doha | P2 - High | 2026-08-12 06:24 | 2026-08-12 06:29 | 5.2 | 2026-08-12 07:10 | 2026-08-12 07:25 | 14.6667 | 60.95 | QBC Team are doing activity at the FP , node restored after activity is done | Completed | Non-maintainer | 3rd Party | QBC(EGIS) | Device Restored | Suhail
742 | Sirti-WAN-R3-Ticket-702 | NA | 2026-08-12 | DC23-ENC102-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 32 | 25.321261° 51.473693° | Inside Doha | P2 - High | 2026-08-12 08:10 | 2026-08-12 08:12 | 2 | 2026-08-12 08:10 | 2026-08-12 08:16 | 5.7667 | 5.7667 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
743 | Sirti-WAN-R3-Ticket-703 | 3972 | 2026-08-12 | P007C2-ENC01-UPE-01 | Adel | Temperature higher than Upper threshold | High Temperature | the team identified that the AC condenser filter was blocked |  | Zone 38 | 25.2931613° 51.4894255° | Inside Doha | P3 - Medium | 2026-08-12 11:33 | 2026-08-12 11:35 | 2 | 2026-08-12 13:30 | 2026-08-12 14:00 | 30 | 147.5833 | Visited the site, checked the power and voltage, cleaned the dusty and blocked AC filters and condenser, checked the gas and all components, and confirmed the AC is cooling and operating properly. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Ghulam
744 | Sirti-WAN-R3-Ticket-704 | 3973 | 2026-08-12 | CRR-ENC30-UPE-02 | Adel | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 24 | 25.268° 51.515° | Inside Doha | P3 - Medium | 2026-08-12 12:24 | 2026-08-12 12:26 | 2 | 2026-08-12 12:24 | 2026-08-12 16:40 | 256.9333 | 256.9333 | Replace the Faulty fan motor and capacitor, cleaned the condenser coil, service the AC | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
745 | Sirti-WAN-R3-Ticket-705 | 3977 | 2026-08-12 | P008C3-ENC01-UPE-01 | Adel | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 55 | 25.2614822° 51.4801647° | Outside Doha | P3 - Medium | 2026-08-12 13:03 | 2026-08-12 13:05 | 2 | 2026-08-12 13:03 | 2026-08-12 13:18 | 15.05 | 15.05 | Visited the site, checked the power and voltage, cleaned the dusty and blocked AC filters and condenser, checked the gas and all components, and confirmed the AC is cooling and operating properly. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
746 | Sirti-WAN-R3-Ticket-706 | NA | 2026-08-12 | P023C2-ENC16-CE-01 | Adel | Link Down | LAN Link Down | The 10G link towards USW XG 0/0/4 is down |  | Zone 82 | 25.228079° 51.307359° | Outside Doha | P3 - Medium | 2026-08-12 14:07 | 2026-08-12 14:10 | 3 | 2026-08-12 14:10 | 2026-08-12 15:04 | 54.1833 | 57.1833 | FLM restarted LAN AMG Switch | Completed | Non-maintainer | No Node Down | LAN SW restarted | Alarm Cleared | -
747 | Sirti-WAN-R3-Ticket-707 | 3963 | 2026-08-12 | P004-ENC43-UPE-02 | Arif | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-08-12 14:41 | 2026-08-12 14:48 | 7 | 2026-08-12 16:58 | 2026-08-12 17:20 | 21.1333 | 158.45 | Visited the site, checked the power, voltage, gas, filters, and condenser. Cleaned the clogged filters and condenser, restarted the AC, and confirmed normal cooling and operation. | Completed | Non-maintainer | Defect | AC | Device Restored | Ghulam
748 | Sirti-WAN-R3-Ticket-708 | 3971 | 2026-08-12 | SAL-TCC-NPE-01 | Arif | Link Down | QNBN Link down (100GE1/3/0/3) to P023C1-ENC01-UPE01 | link is auto restored |  | Zone55 | 25.2088874° 51.4008611° | Outside Doha | P3 - Medium | 2026-08-12 15:43 | 2026-08-12 15:48 | 5 | 2026-08-12 15:48 | 2026-08-12 16:00 | 12.5833 | 17.5833 | Alarm Auto cleared before FLM reach the site | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
749 | Sirti-WAN-R3-Ticket-709 | NA | 2026-08-12 | P007C2-ENC01-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | CB tripped due to an AC rectification issue. |  | Zone 38 | 25.2931613° 51.4894255° | Inside Doha | P2 - High | 2026-08-12 19:41 | 2026-08-12 19:42 | 1 | 2026-08-12 19:42 | 2026-08-12 19:46 | 4 | 5 | CB tripped due to an AC rectification issue. | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | Ghulam
750 | Sirti-WAN-R3-Ticket-710 | NA | 2026-08-13 | P010-ENC64-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Device went down during Planned Sheduled PPM |  | Zone 91 | 25.16822° 51.48128° | Outside Doha | P2 - High | 2026-08-13 04:33 | 2026-08-13 04:35 | 1.3 | 2026-08-13 04:35 | 2026-08-13 04:38 | 3.8 | 5.1 | Device went down during Planned Sheduled PPM | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Eric
751 | Sirti-WAN-R3-Ticket-711 | 3979 | 2026-08-13 | 22FEB-ENC15-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | No power at the WAN cabinet |  | Zone54 | 25.28160814° 51.48539846° | Outside Doha | P2 - High | 2026-08-13 08:04 | 2026-08-13 08:07 | 3 | 2026-08-13 08:25 | 2026-08-13 09:22 | 57.4833 | 78.15 | QBC Team are doing activity at the FP , node restored after activity is done | Completed | Non-maintainer | 3rd Party | QBC(EGIS) | Device Restored | Hichem
752 | Sirti-WAN-R3-Ticket-712 | 3992 | 2026-08-13 | P011-ENC26-UPE-01 | Adel | card stopped working | Hardware alarm | LPU Card Slot 2 was Hanged |  | Zone 91 | 25.19975° 51.541528° | Outside Doha | P3 - Medium | 2026-08-13 13:54 | 2026-08-13 13:56 | 2 | 2026-08-13 16:28 | 2026-08-13 16:39 | 10.45 | 164.45 | Card was reseated/reinserted card communcation was restored and all assocaited alarms cleared | Completed | Maintainer | N/A | N/A | Alarm Cleared | Irshad
753 | Sirti-WAN-R3-Ticket-713 | NA | 2026-08-13 | P010-ENC64-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 91 | 25.16822° 51.48128° | Outside Doha | P2 - High | 2026-08-13 16:39 | 2026-08-13 16:42 | 3 | 2026-08-13 16:39 | 2026-08-13 16:44 | 5.45 | 5.45 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Alarm Cleared | -
754 | Sirti-WAN-R3-Ticket-714 | 3997 | 2026-08-13 | DC23-ENC102-CE-01 | Sanket | Power Module Stopped Working | Power Fault | PWR1 is stopped working |  | Zone 32 | 25.321261° 51.473693° | Inside Doha | P3 - Medium | 2026-08-13 23:26 | 2026-08-13 23:29 | 2.2 | 2026-08-13 23:46 | 2026-08-13 23:51 | 4.7833 | 24.3333 | The CE switch standby power was restored by shifting the supply from the faulty circuit breaker to an available one. | Completed | Maintainer | N/A | N/A | Alarm Cleared | Rizwan
755 | Sirti-WAN-R3-Ticket-715 | NA | 2026-08-15 | P007-TCR-NPE-01 P007C5P1-ENC15-UPE-01 SAL-TCC-NPE-01 P006-ENC17-UPE | Sanket | Link Down | WAN Link Down | Planned activity By QNBN intends to perform permanent rectification on one of the QNBN cable segment |  | Zone 52 | 25.2942202° 51.4657002° | Outside Doha | P3 - Medium | 2026-08-15 01:00 | 2026-08-15 01:02 | 2 | 2026-08-15 04:53 | 2026-08-15 04:54 | 1.25 | 234.5 | Planned activity By QNBN intends to perform permanent rectification on one of the QNBN cable segment | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
756 | Sirti-WAN-R3-Ticket-716 | NA | 2026-08-15 | P023C2-ENC43-CE-01 | AMR | Link Down | LAN Link Down | LAN switch is hanged due to high temp. |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-08-15 14:41 | 2026-08-15 14:43 | 2 | 2026-08-15 16:00 | 2026-08-15 16:15 | 15 | 94.4167 | FLM restarted hanged LAN switch | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
757 | Sirti-WAN-R3-Ticket-717 | NA | 2026-08-15 | SAL-ENC09-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-08-15 17:53 | 2026-08-15 17:54 | 1 | 2026-08-15 17:53 | 2026-08-15 17:55 | 2.5 | 2.5 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
758 | Sirti-WAN-R3-Ticket-718 | 4012 | 2026-08-15 | P006-ENC17-UPE02 | Adel | CPU temperature too High | High Temperature | High Temperature |  | Zone 56 | 25.19614, 51.45325 | Outside Doha | P3 - Medium | 2026-08-15 13:43 | 2026-08-15 13:46 | 3 | 2026-08-15 18:00 | 2026-08-15 18:08 | 8.4333 | 265.3333 | After replacing the compressor and capacitor, the AC is operating normally with proper cooling | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan
759 | Sirti-WAN-R3-Ticket-719 | 4026 | 2026-08-16 | P010-ENC01-UPE01 | AMR | CPU temperature too High | High Temperature | AC was operational, but not cooling |  | Zone 81 | 25.1398815° 51.4073931° | Outside Doha | P3 - Medium | 2026-08-16 14:02 | 2026-08-16 14:03 | 1 | 2026-08-16 15:32 | 2026-08-16 18:50 | 198.15 | 288.3167 | Visited the site, checked power and voltage, cleaned and serviced the dusty/rusty AC filter and unit, refilled R22 gas, reinstalled the AC in the ENC cabinet, and verified that it is now cooling properly and operating normally | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
760 | Sirti-WAN-R3-Ticket-720 | NA | 2026-08-17 | SAL-ENC09-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | P2 - High | 2026-08-17 03:59 | 2026-08-17 04:00 | 1 | 2026-08-17 03:59 | 2026-08-17 04:02 | 2.5167 | 2.5167 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
761 | Sirti-WAN-R3-Ticket-721 | 4037 | 2026-08-17 | 22FEB-ENC13-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | No power at the WAN cabinet |  | Zone 55 | 25.27506948° 51.48993629° | Outside Doha | P2 - High | 2026-08-17 09:34 | 2026-08-17 09:36 | 1.8333 | 2026-08-17 15:30 | 2026-08-17 15:47 | 16.8333 | 372.6667 | The S/L feeder pillar main MCB was found tripped, and the team reset it by switching the main breaker ON. | Completed | Non-maintainer | 3rd Party | Others | Device Restored | Ghulam
762 | Sirti-WAN-R3-Ticket-722 | 4052 | 2026-08-18 | CRR-ENC26-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | No power at the WAN cabinet |  | Zone 41 | 25.26019° 51.52483° | Inside Doha | P2 - High | 2026-08-18 01:02 | 2026-08-18 01:04 | 2 | 2026-08-18 01:19 | 2026-08-18 01:44 | 25.6333 | 42.6333 | FLM switched on tripped CB at FP | Completed | Maintainer | N/A | N/A | Device Restored | Rizwan
763 | Sirti-WAN-R3-Ticket-723 | 4054 | 2026-08-18 | P008C2-ENC42-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Main CB is tripped for WAN cabinet |  | Zone 56 | 25.211892° 51.5391135° | Outside Doha | P2 - High | 2026-08-18 04:25 | 2026-08-18 04:27 | 2 | 2026-08-18 05:02 | 2026-08-18 05:12 | 10.1167 | 47.6 | FLM switched on tripped MAIN CB | Completed | Maintainer | N/A | N/A | Device Restored | hicham
764 | Sirti-WAN-R3-Ticket-724 | NA | 2026-08-18 | P011-ENC31-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 91 | 25.1958474° 51.5452735° | Outside Doha | P2 - High | 2026-08-18 04:39 | 2026-08-18 04:41 | 2 | 2026-08-18 04:39 | 2026-08-18 04:45 | 6.1667 | 6.1667 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
dis 765 | Sirti-WAN-R3-Ticket-725 | 4078 | 2026-08-18 | P008C2-ENC42-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Main CB is tripped for WAN cabinet due to short circuit in AC power cable |  | Zone 56 | 25.211892° 51.5391135° | Outside Doha | P2 - High | 2026-08-18 22:59 | 2026-08-18 23:02 | 3 | 2026-08-18 23:30 | 2026-08-18 23:41 | 10.8167 | 41.5667 | FLM switched on tripped MAIN CB and fixed AC power cable | Completed | Maintainer | N/A | N/A | Device Restored | Rizwan
766 | Sirti-WAN-R3-Ticket-726 | 4083 | 2026-08-18 | P028C2-ENC07-UPE-02 | Adel | Link Down | WAN Link Down | Link is down between P028C2-ENC07-UPE-02 (40GE 3/0/1 ) TO P028C2-ENC16-CE-01 (port 1/25) |  | Zone 06 | 25.2827572° 51.5448455° | Inside Doha | P3 - Medium | 2026-08-18 23:01 | 2026-08-18 23:04 | 3 | 2026-08-18 23:30 | 2026-08-19 05:30 | 360 | 388.95 | FLM replaced damaged fiber cable | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Hassan/Rizwan
767 | Sirti-WAN-R3-Ticket-727 | NA | 2026-08-19 | P010-ENC51-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power interruption |  | Zone 91 | 25.157928° 51.4736335° | Outside Doha | P2 - High | 2026-08-19 03:17 | 2026-08-19 03:19 | 2 | 2026-08-19 03:17 | 2026-08-19 03:23 | 5.7833 | 5.7833 | kahromaa power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
768 | Sirti-WAN-R3-Ticket-728 | NA | 2026-08-19 | P060-ENC179-CE-GME-01 | Sanket | Link Down | LAN Link Down | Ge 1/13 and Ge 1/14 towards AKE-USW-N7-R1 |  | Zone 70 | 25.639484° 51.491537° | Outside Doha | P3 - Medium | 2026-08-19 19:50 | 2026-08-19 19:56 | 6.05 | 2026-08-19 19:57 | 2026-08-19 19:58 | 1.0167 | 8.0667 | The link is down towards LAN and Autorestored. | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | -
769 | Sirti-WAN-R3-Ticket-729 | NA | 2026-08-19 | COR-ENC07-CE-01 | Sanket | Link Down | LAN Link Down | XGE0/0/3 towards QPD-ENC1-BSW1 |  | Zone 63 | 25.31320770235765, 51.52089816892454 | Outside Doha | P3 - Medium | 2026-08-19 21:26 | 2026-08-19 21:28 | 1.2333 | 2026-08-19 21:28 | 2026-08-19 21:30 | 1.1167 | 3.1833 | The link is down towards LAN and Autorestored. | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | -
770 | Sirti-WAN-R3-Ticket-730 | 4094 | 2026-08-20 | P042-ENC08-CE-01.omc.local | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | No power at the WAN cabinet |  | Zone 49 | 25.227332 51.5922796 | Outside Doha | P2 - High | 2026-08-20 01:18 | 2026-08-20 01:22 | 3.7833 | 2026-08-20 01:44 | 2026-08-20 02:08 | 24 | 50.2667 | The AC was down due to a faulty timer output, causing the UPS to overheat and trip the main input breaker. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan
771 | Sirti-WAN-R3-Ticket-731 | NA | 2026-08-20 | SAL-ENC32-CE-01 | Arif | Link Down | RC collector Link down | Ports GE1/0/6 & GE1/0/7 Toward Remote Collector |  | Zone 82 | 25.1165799° 51.1812367° | Outside Doha | P3 - Medium | 2026-08-20 03:05 | 2026-08-20 03:17 | 12.2833 | 2026-08-20 03:05 | 2026-08-20 03:46 | 41.1 | 41.1 | The link is down towards RC Collector and Autorestored. | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | -
772 | Sirti-WAN-R3-Ticket-732 | NA | 2026-08-20 | COR-ENC12-CE-01 | AMR | Link Down | LAN Link Down | ENC02 (LAN Cisco 4K) CB tripped |  | Zone 61 | 25.324005699251956, 51.52792742883553 | Outside Doha | P3 - Medium | 2026-08-20 11:30 | 2026-08-20 11:31 | 1 | 2026-08-20 15:01 | 2026-08-20 15:17 | 16 | 226.9667 | Main CB at ITS FP was tripped. Devices restored after turning CB ON | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Irshad
773 | Sirti-WAN-R3-Ticket-733 | NA | 2026-08-20 | P060-ENC179-CE-GME-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa power intruption |  | Zone 70 | 25.639484° 51.491537° | Outside Doha | P2 - High | 2026-08-20 15:32 | 2026-08-20 15:35 | 3.1 | 2026-08-20 15:35 | 2026-08-20 15:36 | 1.1167 | 4.4667 | Kahramaa power intruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
774 | Sirti-WAN-R3-Ticket-734 | NA | 2026-08-20 | P007C2-ENC59-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | CB Tripped during PPM |  | Zone 54 | 25.2922123° 51.4648447° | Outside Doha | P2 - High | 2026-08-20 16:52 | 2026-08-20 16:54 | 2 | 2026-08-20 16:55 | 2026-08-20 16:56 | 1.05 | 4.05 | CB Tripped during PPM | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Khader
775 | Sirti-WAN-R3-Ticket-735 | NA | 2026-08-20 | DC23-ENC102-CE-01 | Sanket | Power Module Stopped Working | Power Fault | CB changed during PPM |  | Zone 32 | 25.321261° 51.473693° | Inside Doha | P3 - Medium | 2026-08-20 21:49 | 2026-08-20 21:50 | 1.05 | 2026-08-20 21:51 | 2026-08-20 21:52 | 0.76667 | 2.8167 | CB changed during PPM | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | Rizwan
776 | Sirti-WAN-R3-Ticket-736 | NA | 2026-08-20 | COR-ENC12-CE-01 | Sanket | Link Down | LAN Link Down | CB Tripped during PPM at QPD-ENC5 |  | Zone 61 | 25.324005699251956, 51.52792742883553 | Outside Doha | P3 - Medium | 2026-08-20 22:03 | 2026-08-20 22:04 | 1.05 | 2026-08-20 22:05 | 2026-08-20 22:06 | 0.71667 | 2.75 | CB Tripped during PPM at QPD-ENC5 | Completed | Non-maintainer | Planned Activity | PPM | Alarm Cleared | Ghulam
777 | Sirti-WAN-R3-Ticket-737 | 4124 | 2026-08-21 | DC23-ENC102-CE-01 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | The MCB tripped at Feeder Piller |  | Zone 32 | 25.321261° 51.473693° | Inside Doha | P2 - High | 2026-08-21 13:53 | 2026-08-21 13:55 | 2 | 2026-08-21 15:30 | 2026-08-21 16:42 | 72.3 | 169.6167 | The MCB tripped at SLFP | Completed | Non-maintainer | 3rd Party | SLFP | Device Restored | Ghulam
778 | Sirti-WAN-R3-Ticket-738 | 4128 | 2026-08-22 | P005-ENC414-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | Device was energized by generator |  | Zone 51 | 25.3335964° 51.4482522° | Outside Doha | P2 - High | 2026-08-22 01:31 | 2026-08-22 01:37 | 5.7833 | 2026-08-22 02:07 | 2026-08-22 02:58 | 50.8333 | 86.7333 | Disconnected the power generator and connected back KAHRAMAA power source. KAHRAMAA Reference No.: 261100046956. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | Rizwan
779 | Sirti-WAN-R3-Ticket-739 | 4132 | 2026-08-22 | P059C1-N2-ENC01-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | No power at the WAN cabinet |  | Zone 70 | 25.65464719 51.39220104 | Outside Doha | P2 - High | 2026-08-22 06:56 | 2026-08-22 06:58 | 1.75 | 2026-08-22 08:00 | 2026-08-22 08:03 | 3.2 | 66.95 | QBC Team are doing activity at the FP , node restored after activity is done | Completed | Non-maintainer | 3rd Party | QBC(EGIS) | Device Restored | Hichem
780 | Sirti-WAN-R3-Ticket-740 | NA | 2026-08-24 | P028C2-ENC04-CE-01.omc.local | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa power intruption |  | Zone 13 | 25.2791625° 51.5290008° | Inside Doha | P2 - High | 2026-08-24 20:13 | 2026-08-24 20:16 | 3 | 2026-08-24 20:13 | 2026-08-24 20:22 | 9.7 | 9.7 | Kahramaa power intruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
781 | Sirti-WAN-R3-Ticket-741 | NA | 2026-08-24 | P005-TCR-UPE-01 | Adel | Power Module Stopped Working | Power alarm | GBDG Team are doing activity ON SITE |  | Zone 55 | 25.3199307° 51.447548° | Outside Doha | P3 - Medium | 2026-08-24 20:03 | 2026-08-24 20:05 | 2 | 2026-08-24 20:03 | 2026-08-24 21:46 | 103.2 | 103.2 | GBDG Team are doing activity ON SITE , Alarm is cleared after activity is completed | Completed | Non-maintainer | 3rd Party | GBDG(EGIS) | Device Restored | Hassan
782 | Sirti-WAN-R3-Ticket-742 | 4181 | 2026-08-24 | P005-TCR-UPE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | GBDG Team are doing activity ON SITE |  | Zone 55 | 25.3199307° 51.447548° | Outside Doha | P2 - High | 2026-08-24 20:43 | 2026-08-24 20:45 | 2 | 2026-08-24 20:43 | 2026-08-24 21:02 | 18.4833 | 18.4833 | GBDG Team are doing activity ON SITE | Completed | Non-maintainer | 3rd Party | GBDG(EGIS) | Device Restored | Hassan
783 | Sirti-WAN-R3-Ticket-743 | 4182 | 2026-08-24 | P004-ENC19-CE-01 | Adel | Power fault | Power alarm | CB was found tripped |  | Zone 53 | 25.3163497° 51.3511125° | Outside Doha | P3 - Medium | 2026-08-24 20:08 | 2026-08-24 20:10 | 2 | 2026-08-24 22:30 | 2026-08-24 22:51 | 21.15 | 163.1 | CB was found tripped | Completed | Maintainer | N/A | N/A | Alarm Cleared | Rizwan
784 | Sirti-WAN-R3-Ticket-744 | 4188 | 2026-08-25 | 22FEB-ENC15-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | No PWR at FP/QBC Team are doing activity at the FP |  | Zone 54 | 25.28160814° 51.48539846° | Outside Doha | P2 - High | 2026-08-25 06:09 | 2026-08-25 06:12 | 3.25 | 2026-08-25 06:49 | 2026-08-25 08:36 | 106.7833 | 147.1167 | The FLM team has connected the generator set to the feeder pillar temporarily until the QBC team completes its activities at the feeder pillar. | Completed | Non-maintainer | 3rd Party | QBC(EGIS) | Device Restored | ERIC
785 | Sirti-WAN-R3-Ticket-745 | NA | 2026-08-25 | P005-TCR-UPE-01 | AMR | Power Module Stopped Working | Power alarm | GBDG Team are doing activity ON SITE |  | Zone 55 | 25.3199307° 51.447548° | Outside Doha | P3 - Medium | 2026-08-25 11:45 | 2026-08-25 11:46 | 1 | 2026-08-25 11:45 | 2026-08-25 11:46 | 1.3167 | 1.3167 | GBDG Team are doing activity ON SITE | Completed | Non-maintainer | 3rd Party | GBDG(EGIS) | Device Restored | -
786 | Sirti-WAN-R3-Ticket-746 | 4208 | 2026-08-26 | 22FEB-ENC13-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Egis team is doing activity near the site |  | Zone 55 | 25.27506948° 51.48993629° | Outside Doha | P2 - High | 2026-08-26 07:03 | 2026-08-26 07:05 | 2 | 2026-08-26 08:00 | 2026-08-26 08:43 | 43.1667 | 99.9 | FLM connected temporary PG to restore the node till activity is done by Egis | Completed | Non-maintainer | 3rd Party | QBC(EGIS) | Device Restored | ERIC
787 | Sirti-WAN-R3-Ticket-747 | 4209 | 2026-08-26 | CRR-ENC37-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no Kahromaa power at FP |  | Zone 23 | 25.265846° 51.500562° | Inside Doha | P2 - High | 2026-08-26 07:29 | 2026-08-26 07:32 | 3 | 2026-08-26 08:10 | 2026-08-26 08:53 | 43.3333 | 84.7667 | FLM connected temporary PG to restore the node till kahromaa power is restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Restored | Umair
788 | Sirti-WAN-R3-Ticket-748 | 4222 | 2026-08-26 | 22FEB-ENC13-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The Egis team is carrying out an activity in the FP. |  | Zone 55 | 25.27506948° 51.48993629° | Outside Doha | P2 - High | 2026-08-26 15:41 | 2026-08-26 15:44 | 3 | 2026-08-26 15:51 | 2026-08-26 15:53 | 1.25 | 11.3333 | The Egis team is carrying out an activity in the FP. | Completed | Non-maintainer | 3rd Party | QBC(EGIS) | Device Restored | Khader
789 | Sirti-WAN-R3-Ticket-749 | NA | 2026-08-26 | P001-ENC02-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | CB Tripped during PPM |  | Zone 56 | 25.21911, 51.52039 | Outside Doha | P2 - High | 2026-08-26 17:09 | 2026-08-26 17:14 | 5.05 | 2026-08-26 17:16 | 2026-08-26 17:16 | 0.78333 | 7.45 | CB Tripped during PPM | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Khader
790 | Sirti-WAN-R3-Ticket-750 | 4250 | 2026-08-27 | P028C2-ENC25-UPE-01 P028C2-ENC07-UPE-02 | AMR | Link Down | WAN Link Down | QNBN Team disconnected the link as per Ashghal |  | Zone 13 | 25.2898333° 51.5151388° | Inside Doha | P3 - Medium | 2026-08-27 08:39 | 2026-08-27 08:44 | 5 | 2026-08-27 09:20 | 2026-08-27 15:37 | 377.1167 | 418.5667 | after communication with QNBN Team , they reconnected the link back , alarm is got clear | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | Umair
791 | Sirti-WAN-R3-Ticket-751 | NA | 2026-08-28 | P023C2-ENC16-CE-01 | Sanket | Link Down | LAN Link Down | Port XG 0/0/4 towards USW4 is down |  | Zone 82 | 25.228079° 51.307359° | Outside Doha | P3 - Medium | 2026-08-28 14:34 | 2026-08-28 14:39 | 5.1667 | 2026-08-28 14:34 | 2026-08-28 15:06 | 31.7 | 31.7 | Link is auto restored before FLM reaching site | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
792 | Sirti-WAN-R3-Ticket-752 | 4286 | 2026-08-29 | P061-ENC13-CE-01 | Adel | Optical model temprature too high | High Temperature | Ac is not working |  | Zone 55 | 25.263460° 51.459387° | Outside Doha | P3 - Medium | 2026-08-29 11:35 | 2026-08-29 11:39 | 4 | 2026-08-29 11:35 | 2026-08-29 14:49 | 194.8833 | 194.8833 | AC controller was reset, thermostat and refrigerant levels adjusted, and filters cleaned. The AC was tested and is now operating properly. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Rizwan
793 | Sirti-WAN-R3-Ticket-753 | NA | 2026-08-29 | P023C2-ENC16-CE-01 | Adel | Link Down | LAN Link Down | Port XG 0/0/4 towards USW4 was down |  | Zone 82 | 25.228079° 51.307359° | Outside Doha | P3 - Medium | 2026-08-29 14:21 | 2026-08-29 14:25 | 4 | 2026-08-29 14:21 | 2026-08-29 15:28 | 66.5667 | 66.5667 | Link is auto restored before FLM reaching site | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | -
794 | Sirti-WAN-R3-Ticket-754 | NA | 2026-08-29 | P009C1-ENC13-CE-01 | Aaqib | Optical model temprature too high | High Temperature | AC compressor is faulty |  | Zone 55 | 25.24424° 51.43135° | Outside Doha | P3 - Medium | 2026-08-29 15:08 | 2026-08-29 15:13 | 5.0333 | 2026-08-29 15:08 | 2026-08-29 15:54 | 45.1167 | 45.1167 | AC compressor is faulty. Team will arrange AC acompressor. FAN is operational now | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Ghulam
795 | Sirti-WAN-R3-Ticket-755 | NA | 2026-08-30 | P059C1-ENC51-CE-01 | Adel | Optical model temprature too high | High Temperature | AC was off due to timer is not adjusted |  | Zone 74 | 25.624509° 51.39970937° | Outside Doha | P3 - Medium | 2026-08-30 06:42 | 2026-08-30 06:46 | 4 | 2026-08-30 08:19 | 2026-08-30 09:02 | 43.5 | 140.8667 | FLM adjusted timer to operate the AC , if alarm is reported again , team will change timer | Completed | Non-maintainer | Defect | AC | Alarm Cleared | ERIC
796 | Sirti-WAN-R3-Ticket-756 | NA | 2026-08-30 | P003-ENC40-UPE-02 | Adel | CPU temperature too High | High Temperature | Air filter was blocked. Required cleaning |  | Zone 63 | 25.3344995° 51.5180512° | Outside Doha | P3 - Medium | 2026-08-30 12:40 | 2026-08-30 12:44 | 4 | 2026-08-30 12:40 | 2026-08-30 14:07 | 86.1667 | 86.1667 | The AC filter was found completely blocked, causing the compressor to overheat and stop. The filter and condenser coil were cleaned using a blower and pressure water. After servicing, the AC resumed normal operation and cooling was restored | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Ghulam
797 | Sirti-WAN-R3-Ticket-757 | 4299 | 2026-08-30 | CRR-ENC46-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | MCB was found tripped inside Cabinet |  | Zone 50 | 25.22608° 51.57875° | Outside Doha | P2 - High | 2026-08-30 13:28 | 2026-08-30 13:29 | 1 | 2026-08-30 15:39 | 2026-08-30 15:44 | 4.95 | 136 | MCB was found tripped. Team turned on and device restored | Completed | Maintainer | MCB tripped | MCB | Device Restored | Khadar
798 | Sirti-WAN-R3-Ticket-758 | NA | 2026-08-30 | COR-ENC12-UPE-02 | Adel | Temperature higher than Upper threshold | High Temperature | Found dusty and blocked air filters and condenser, restricting airflow |  | Zone 61 | 25.324005699251956, 51.52792742883553 | Outside Doha | P3 - Medium | 2026-08-30 13:46 | 2026-08-30 13:49 | 3 | 2026-08-30 13:46 | 2026-08-30 15:34 | 107.8333 | 107.8333 | Visited the site and checked power cables, voltage, gas, and overall AC condition. Found dusty/blocked filters and condenser. Cleaned the filters and AC unit thoroughly. AC is now cooling properly and working normally. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
799 | Sirti-WAN-R3-Ticket-759 | NA | 2026-08-30 | P040-CPE-01-ENC01-DSW | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa power intruption |  | Zone 81 | 25.179715° 51.408779° | Outside Doha | P2 - High | 2026-08-30 16:32 | 2026-08-30 16:35 | 3.1333 | 2026-08-30 16:32 | 2026-08-30 16:41 | 9.0167 | 9.0167 | Kahramaa power intruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
800 | Sirti-WAN-R3-Ticket-760 | NA | 2026-08-30 | COR-ENC12-CE-01 COR-ENC12-UPE-02 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | MCB tripped during AC troubleshooting |  | Zone 61 | 25.324005699251956, 51.52792742883553 | Outside Doha | P3 - Medium | 2026-08-30 18:33 | 2026-08-30 18:35 | 2.15 | 2026-08-30 18:33 | 2026-08-30 18:39 | 5.8833 | 5.8833 | MCB tripped during AC troubleshooting | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Khadar
801 | Sirti-WAN-R3-Ticket-761 | 4310 | 2026-08-30 | P002-ENC07-UPE-01 | Aaqib | card stopped working | Card stuck | Card was hanging repeatedly /LPU card 3 |  | Zone 55 | 25.25662° 51.48560° | Outside Doha | P3 - Medium | 2026-08-30 22:23 | 2026-08-30 22:24 | 1.4167 | 2026-08-30 22:23 | 2026-08-30 22:24 | 1.6833 | 1.6833 | LPU3 -Card was JOJI and filters were cleaned | Completed | Maintainer | Hardware Issue | Hardware | Alarm Cleared | Ghulam
802 | Sirti-WAN-R3-Ticket-762 | 4311 | 2026-08-31 | COR-ENC01-CE-01 | Arif | Link Down | WAN Link Down | Patch coard was faulty |  | Zone 13 | 25.2899979° 51.5487964° | Inside Doha | P3 - Medium | 2026-08-31 00:57 | 2026-08-31 01:02 | 4.85 | 2026-08-31 01:18 | 2026-08-31 01:28 | 10.6167 | 31.1667 | Replaced the patch cord cables at COR-ENC01-CE-01 (interface XG0/1/1) | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Rizwan
803 | Sirti-WAN-R3-Ticket-763 | 4326 | 2026-08-31 | P059C1-ENC51-CE-01 | Adel | Optical model temprature too high | High Temperature | AC was off due to timer relay is fault |  | Zone 74 | 25.624509° 51.39970937° | Outside Doha | P3 - Medium | 2026-08-31 07:14 | 2026-08-31 07:16 | 2 | 2026-08-31 10:45 | 2026-08-31 12:07 | 82.45 | 293.2 | FLM replaced faulty timer relay | Completed | Non-maintainer | Defect | AC | Alarm Cleared | ERIC
804 | Sirti-WAN-R3-Ticket-764 | NA | 2026-08-31 | DC23-ENC104-CE-01 | Adel | Optical model temprature too high | High Temperature | Compressor not working. PCB board was reconnected |  | Zone 51 | 25.320812° 51.469483° | Outside Doha | P3 - Medium | 2026-08-31 13:27 | 2026-08-31 13:30 | 3 | 2026-08-31 13:27 | 2026-08-31 15:44 | 137.05 | 137.05 | Checked power and voltage at site. Found AC compressor unavailable and PCB faulty. Connected the circulation fan to the MCB, and the cabinet is now cooling. Note: AC compressor to be purchased and installed later. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
805 | Sirti-WAN-R3-Ticket-765 | 4336 | 2026-08-31 | P060 DWDM Sec | Aaqib | OCS_LOS | DWDM Link down | Fiber cut near P060 Control room junction |  | Zone 70 | 25.545418° 51.446774° | Outside Doha | P3 - Medium | 2026-08-31 19:32 | 2026-08-31 19:40 | 7.8667 | 2026-08-31 21:47 | 2026-08-31 22:30 | 42.4167 | 177.5 | As per QNBN NOC, there was fiber cut near P060 junction-QNBN TT#16489 | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | QNBN/Hassan
806 | Sirti-WAN-R3-Ticket-766 | NA | 2026-08-31 | P005-ENC402-UPE02 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | MCB tripped during AC troubleshooting |  | Zone 53 | 25.306965° 51.40753° | Outside Doha | P2 - High | 2026-08-31 21:05 | 2026-08-31 21:08 | 2.2 | 2026-08-31 21:05 | 2026-08-31 21:12 | 6.1667 | 6.1667 | MCB tripped during AC troubleshooting. | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Khadar
807 | Sirti-WAN-R3-Ticket-767 | NA | 2026-08-31 | P040-CPE-01-ENC01-DSW | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa power intruption |  | Zone 81 | 25.179715° 51.408779° | Outside Doha | P2 - High | 2026-08-31 21:53 | 2026-08-31 21:55 | 2.1333 | 2026-08-31 21:53 | 2026-08-31 21:57 | 4.0167 | 4.0167 | Kahramaa power intruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
808 | Sirti-WAN-R3-Ticket-768 | 4342 | 2026-09-01 | P007C7P1-ENC10-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | No power in the Cabinet ABB TruONE OTM Transfer Switch not working in Fidder Piller |  | Zone 30 | 25.3474352° 51.4651773° | Inside Doha | P2 - High | 2026-09-01 04:55 | 2026-09-01 05:02 | 6.15 | 2026-09-01 05:19 | 2026-09-01 09:32 | 252.9167 | 276.8833 | FLM checked the FP and found that the ABB TruONE OTM Transfer Switch was not functioning. FLM bypassed the transfer switch inside the FP and restored the power supply.The voltage received at the cabinet was 400V. FLM raised a complaint with Kahramaa under Complaint No. 261100045143.To restore the CE device, FLM temporarily connected the PG power source.The CE Power Module A was found faulty due to the high voltage. FLM therefore connected the power supply to Power Module B and restored the CE device. | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Suhail
809 | Sirti-WAN-R3-Ticket-769 | NA | 2026-09-01 | P040-CPE01-ENC01-DSW | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa power intruption |  | Zone 81 | 25.179715° 51.408779 | Outside Doha | P2 - High | 2026-09-01 10:10 | 2026-09-01 10:11 | 0.56667 | 2026-09-01 10:10 | 2026-09-01 10:13 | 2.9833 | 2.9833 | Kahramaa power intruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
810 | Sirti-WAN-R3-Ticket-770 | NA | 2026-09-01 | P007C7P1-ENC10-CE-01 P007C7P1-ENC03-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | The FLM team inspected the switch and found that the power cable was damaged. |  | Zone 30 | 25.3474352° 51.4651773° | Inside Doha | P2 - High | 2026-09-01 18:45 | 2026-09-01 18:46 | 0.51667 | 2026-09-01 18:47 | 2026-09-01 21:06 | 138.6333 | 140.15 | P007C7P1-ENC10-CE-01-The damaged switch power cable was replaced by the FLM team, and the power supply to the switch has been successfully restored. The device is now operational. | Completed | Maintainer | N/A | N/A | Device Restored | Ghulam
811 | Sirti-WAN-R3-Ticket-771 | NA | 2026-09-02 | P059C1-N2-ENC01-CE-01 | Adel | Link Down | LAN Link Down | alarm is autorestored before team reach the site |  | Zone 70 | 25.65464719 51.39220104 | Outside Doha | P3 - Medium | 2026-09-02 07:45 | 2026-09-02 07:49 | 4 | 2026-09-02 07:45 | 2026-09-02 07:53 | 7.8833 | 7.8833 | alarm is autorestored before team reach the site | Completed | Non-maintainer | N/A | N/A | Alarm Cleared | -
812 | Sirti-WAN-R3-Ticket-772 | NA | 2026-09-02 | P040-CPE-01-ENC01-DSW | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | - | Zone 81 | 25.179715 51.408779 | Outside Doha | P2 - High | 2026-09-02 15:20 | 2026-09-02 15:21 | 1 | 2026-09-02 15:20 | 2026-09-02 15:25 | 5.3333 | 5.3333 | Kahramaa power intruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
813 | Sirti-WAN-R3-Ticket-773 | 4378 | 2026-09-02 | RMC_toMV2_sec | Arif | IN PWR LOW | DWDM Link down | Input Low power 100GE link |  | Zone 70 | 25.550630° 51.43908° | Inside Doha | P3 - Medium | 2026-09-02 17:28 | 2026-09-02 17:38 | 10 | 2026-09-02 20:18 | 2026-09-02 20:30 | 12.8333 | 182.75 | QNBN team tested the fiber and confirmed it is clean and within acceptable parameters. | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | Hassan
814 | Sirti-WAN-R3-Ticket-774 | NA | 2026-09-02 | MV2-ENC-NPE-01 | Arif | Link Down | DWDM Link down | QNBN Link Down |  | Zone 70 | 25.550630° 51.43908° | Inside Doha | P3 - Medium | 2026-09-02 19:47 | 2026-09-02 19:49 | 2.2333 | 2026-09-02 20:18 | 2026-09-02 20:22 | 4.5667 | 35.45 | QNBN team tested the fiber and confirmed it is clean and within acceptable parameters. | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | Hassan
815 | Sirti-WAN-R3-Ticket-775 | 4384 | 2026-09-03 | DUK-ENC30-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | No khahrama power available at site |  | Zone 85 | 25.4637854° 50.930279° | Outside Doha | P2 - High | 2026-09-03 09:09 | 2026-09-03 09:14 | 4.8667 | 2026-09-03 10:16 | 2026-09-03 13:49 | 212.8 | 279.4833 | Khahrama power outage. Ticket # 261100050324 registered. | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | Umair
816 | Sirti-WAN-R3-Ticket-776 | NA | 2026-09-03 | P007C5P1-ENC31-CE-01 | Arif | Link Down | LAN Link Down | LAN switch was hanged due to overheat |  | Zone 54 | 25.27835° 51.4693505° | Inside Doha | P3 - Medium | 2026-09-03 15:16 | 2026-09-03 15:26 | 9.9333 | 2026-09-03 16:07 | 2026-09-03 16:15 | 7.9833 | 58.45 | FLM restarted hanged LAN switch | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadir
817 | Sirti-WAN-R3-Ticket-777 | NA | 2026-09-03 | P028C2-ENC04-CE-01.omc.local | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | CB Tripped during PPM |  | Zone 13 | 25.2791625° 51.5290008° | Inside Doha | P2 - High | 2026-09-03 20:04 | 2026-09-03 20:04 | 1 | 2026-09-03 20:06 | 2026-09-03 20:11 | 5.5 | 7.5 | CB Tripped during PPM | Completed | Non-maintainer | Planned Activity | PPM | Device Restored | Rizwan
818 | Sirti-WAN-R3-Ticket-778 | 4415 | 2026-09-05 | P007C2-170018-R2-CSW | Aaqib | Link Down | LAN Link Down | Links down due to LAN switch hanged |  | Zone 52 | 25.2942202 51.4657002 | Outside Doha | P3 - Medium | 2026-09-05 11:26 | 2026-09-05 11:31 | 5.6667 | 2026-09-05 18:44 | 2026-09-05 19:38 | 53.9333 | 492.15 | TCCMGMT device went down due to a loose power cable. | Completed | Non-maintainer | 3rd Party | STE team | Alarm Cleared | Khadir
819 | Sirti-WAN-R3-Ticket-779 | NA | 2026-09-05 | P008C3-ENC25-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 56 | 25.2341068° 51.50261° | Outside Doha | P2 - High | 2026-09-05 22:41 | 2026-09-05 22:41 | 0 | 2026-09-05 22:42 | 2026-09-05 22:43 | 0.58333 | 1.4833 | Kahramaa power intruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
820 | Sirti-WAN-R3-Ticket-780 | 4416 | 2026-09-06 | SAL-ENC04-CE-01 | Adel | Link Down | LAN Link down | Port down interface GE 1/0/10 connected to Local Device |  | Zone 57 | 25.2204517° 51.4230388° | Outside Doha | P3 - Medium | 2026-09-06 00:40 | 2026-09-06 00:45 | 5 | 2026-09-06 01:43 | 2026-09-06 01:57 | 14.3833 | 77.7 | ITS team is working on CCTV witch is connected to the CE , alarm is cleared after activity is done | Completed | Non-maintainer | 3rd Party | ITSQ | Alarm Cleared | Hassan
821 | Sirti-WAN-R3-Ticket-781 | 4418 | 2026-09-06 | P059C1-N2-ENC01-CE-01 | Aaqib | Low Rx Power | Low Rx Power at LAN link | contamination on Fiber connectors |  | Zone 70 | 25.65464719 51.39220104 | Outside Doha | P3 - Medium | 2026-09-06 07:02 | 2026-09-06 07:07 | 5.2667 | 2026-09-06 07:35 | 2026-09-06 07:41 | 5.6 | 38.7 | Low Rx power due to contaminated fiber connectors. Team cleaned them, and the issue was resolved. | Completed | Non-maintainer | N/A | Fiber | Alarm Cleared | Suhail
822 | Sirti-WAN-R3-Ticket-782 | NA | 2026-09-06 | MV2 to RMC_Sec | Sanket | IN PWR LOW | DWDM Link down | link is auto restored |  | Zone 70 | 25.550630° 51.43908° | Inside Doha | P3 - Medium | 2026-09-06 20:17 | 2026-09-06 20:20 | 3.1667 | 2026-09-06 20:21 | 2026-09-06 20:21 | 0.53333 | 4.4833 | alarm is autorestored before team reach the site | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared
823 | Sirti-WAN-R3-Ticket-783 | 4456 | 2026-09-07 | P002-ENC14-UPE-02 | Aaqib | Temperature higher than Upper threshold | High Temperature | The team identified that the AC filter was blocked |  | Zone 55 | 25.249° 51.471° | Outside Doha | P3 - Medium | 2026-09-07 12:05 | 2026-09-07 12:12 | 7.1 | 2026-09-07 15:35 | 2026-09-07 16:03 | 28.3833 | 238.2 | The team clean the AC filter | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Ghulam
824 | Sirti-WAN-R3-Ticket-784 | 4554 | 2026-09-07 | CRR-ENC46-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found RCCB Tripped |  | Zone 50 | 25.22608° 51.57875° | Outside Doha | P2 - High | 2026-09-07 13:36 | 2026-09-07 13:41 | 4.25 | 2026-09-07 15:36 | 2026-09-07 16:08 | 31.9333 | 151.1667 | FLM turned on the RCCB and device is restored | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Khadar
825 | Sirti-WAN-R3-Ticket-785 | NA | 2026-09-07 | P059C1-N3-ENC33-CE-01 | Sanket | Link Down | LAN Link down | port XG 0/0/2 towards MS79-EXP0253-ITS-ISW-00007 |  | Zone 70 | 25.53313695° 51.41207372° | Outside Doha | P3 - Medium | 2026-09-07 17:41 | 2026-09-07 17:42 | 1.0167 | 2026-09-07 17:42 | 2026-09-07 17:43 | 1.0167 | 2.3167 | Link is auto restored before FLM reaching site | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | -
826 | Sirti-WAN-R3-Ticket-786 | NA | 2026-09-07 | P040-CPE01-ENC01-DSW | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 81 | 25.179715° 51.408779° | Outside Doha | P2 - High | 2026-09-07 19:45 | 2026-09-07 19:46 | 1 | 2026-09-07 19:47 | 2026-09-07 19:48 | 1 | 3 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
827 | Sirti-WAN-R3-Ticket-787 | 4461 | 2026-09-07 | MV2-ENC-NPE-01 | Adel | Link Down | WAN Link Down | Link down towards P007-ENC-P-01 via DWDM |  | Zone 70 | 25.550630° 51.43908° | Outside Doha | P3 - Medium | 2026-09-07 23:34 | 2026-09-07 23:35 | 1 | 2026-09-07 23:34 | 2026-09-07 23:52 | 17.4167 | 17.4167 | FLM performed OTDR test on link and found high loss on patch cord (length 140m) FLM respliced the patch cord at MV2 ( datahall 1 _ EL10 ) | Completed | Maintainer | N/A | N/A | Alarm Cleared | Rizwan
828 | Sirti-WAN-R3-Ticket-788 | NA | 2026-09-08 | CRR-ENC46-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 50 | 25.22608° 51.57875° | Outside Doha | P2 - High | 2026-09-08 02:39 | 2026-09-08 02:40 | 1 | 2026-09-08 02:39 | 2026-09-08 02:44 | 5.1333 | 5.1333 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
829 | Sirti-WAN-R3-Ticket-789 | NA | 2026-09-08 | CRR-ENC02-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption |  | Zone 18 | 25.2834083° 51.5496912° | Inside Doha | P2 - High | 2026-09-08 09:11 | 2026-09-08 09:12 | 1 | 2026-09-08 09:11 | 2026-09-08 09:16 | 5.15 | 5.15 | KAHRAMAA power interruption | Completed | Non-maintainer | 3rd Party | Kahramaa | Device Restored | -
830 | Sirti-WAN-R3-Ticket-790 | 4513 | 2026-09-08 | P007C2-ENC01-UPE-01 | Sanket | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 38 | 25.2931613° 51.4894255° | Inside Doha | P3 - Medium | 2026-09-08 12:20 | 2026-09-08 12:33 | 12.8667 | 2026-09-08 16:11 | 2026-09-08 16:19 | 8.25 | 239.0333 | FLM cleaned AC filter which was blocked by dust , now AC is colling fine | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Ghulam
831 | Sirti-WAN-R3-Ticket-791 | 4500 | 2026-09-08 | P007C2-ENC99-UPE-02 | Sanket | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 52 | 25.2967109° 51.4488814° | Outside Doha | P3 - Medium | 2026-09-08 12:06 | 2026-09-08 12:16 | 10 | 2026-09-08 16:40 | 2026-09-08 16:41 | 1 | 274.3333 | Visited the site and checked the power supply, voltage, AC filters, and condenser. The filters and AC unit were cleaned, and the gas level was checked. The AC is now cooling properly and operating normally. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
832 | Sirti-WAN-R3-Ticket-792 | 4506 | 2026-09-08 | P014-ENC01-UPE-01 | Sanket | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 57 | 25.254092° 51.513914° | Outside Doha | P3 - Medium | 2026-09-08 12:52 | 2026-09-08 13:03 | 11 | 2026-09-08 14:02 | 2026-09-08 14:10 | 7.5333 | 77.6667 | The AC and UP unit filters were very dirty and cleaned properly. After cleaning, the airflow and cooling improved, and the temperature returned to normal. | Completed | Non-maintainer | 3rd Party | SALAM TECH. | Alarm Cleared | Rizwan
833 | Sirti-WAN-R3-Ticket-793 | NA | 2026-09-08 | P023C2-ENC43-CE-01 | Arif | Link Down | LAN Link Down | LAN switch is hanged due to high temp. |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-09-08 14:42 | 2026-09-08 14:49 | 7 | 2026-09-08 15:47 | 2026-09-08 15:48 | 1.2667 | 66.5833 | AMG LAN Switch was hanged due to high temperature inside cabinet | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
834 | Sirti-WAN-R3-Ticket-794 | 4497 | 2026-09-08 | P004-ENC43-UPE-02 | Arif | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-09-08 14:45 | 2026-09-08 14:48 | 2.95 | 2026-09-08 15:35 | 2026-09-08 15:44 | 8.4667 | 58.6833 | Visited site, checked power and voltage, cleaned dusty/blocked AC filters and condenser, and checked gas and overall operation. AC is now cooling properly and functioning normally. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khadar
835 | Sirti-WAN-R3-Ticket-795 | 4501 | 2026-09-08 | P002-ENC13-CE-01 | Arif | FAN Hardware Fault | FAN Faullt | FAN was Hanged |  | Zone 58 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-09-08 16:38 | 2026-09-08 16:39 | 1 | 2026-09-08 17:42 | 2026-09-08 17:56 | 14.1 | 77.65 | Removed Fan 2 from the switch, cleaned it thoroughly, and reinstalled it. Fan 2 is now working normally. | Completed | Maintainer | N/A | N/A | Alarm Cleared | Irshad
836 | Sirti-WAN-R3-Ticket-796 | NA | 2026-09-08 | P060-ENC05-CE-GME-01.omc.local | Arif | Link Down | LAN Link Down | CB was tripped for LAN cabinet |  | Zone 58 | 25.3930278° 51.498346° | Outside Doha | P3 - Medium | 2026-09-08 17:54 | 2026-09-08 17:56 | 2.15 | 2026-09-08 18:50 | 2026-09-08 19:00 | 10.8833 | 66.55 | FLM Switched on tripped CB inside LAN cabinet | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared | Irshad
837 | Sirti-WAN-R3-Ticket-797 | 4518 | 2026-09-09 | P006-ENC02-UPE-01 | Arif | CPU temperature too High | High Temperature | AC evaporator fan motor and capacitor |  | Zone 56 | 25.2190399° 51.4369501° | Outside Doha | P3 - Medium | 2026-09-09 08:51 | 2026-09-09 08:55 | 3.7333 | 2026-09-09 09:36 | 2026-09-09 09:39 | 2.3833 | 47.5 | AC team replaced the AC evaporator fan motor and capacitor. The AC unit was also thoroughly cleaned. and the unit is now working properly and providing cooling. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
838 | Sirti-WAN-R3-Ticket-798 | 4536 | 2026-09-09 | P011-ENC58-CE-01 | Arif | Communication betweeen NMS and NE is Abnormal | Device Down | UPS issue |  | Zone 49 | 25.2273162° 51.5921766° | Outside Doha | P2 - High | 2026-09-09 11:46 | 2026-09-09 11:51 | 4.8833 | 2026-09-09 15:53 | 2026-09-09 16:11 | 18.2167 | 265.1 | After Resetting the UPS, the issue was resolved | Completed | Non-maintainer | Environmental | Heat summer | Device Restored | Najeeb/Ghulam
839 | Sirti-WAN-R3-Ticket-799 | NA | 2026-09-09 | P002-ENC14-UPE-02 | Arif | Temperature higher than Upper threshold | High Temperature | AC was operational, but not cooling |  | Zone 55 | 25.249° 51.471° | Outside Doha | P3 - Medium | 2026-09-09 12:37 | 2026-09-09 12:40 | 3 | 2026-09-09 14:36 | 2026-09-09 14:37 | 1.05 | 119.6333 | During troubleshooting, the team found the AC unit filter and UPE filter blocked. The team cleaned both filters using a blower and adjusted the temperature parameters. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Ghulam
840 | Sirti-WAN-R3-Ticket-800 | 4545 | 2026-09-09 | 22FEB-ENC25-UPE-02 | Arif | Temperature higher than Upper threshold | High Temperature | AC not cooling and OLP was found faulty |  | Zone 51 | 25.338322° 51.449241° | Outside Doha | P3 - Medium | 2026-09-09 13:39 | 2026-09-09 13:45 | 5.8167 | 2026-09-09 14:51 | 2026-09-09 14:53 | 1.85 | 73.6667 | Faulty OLP replaced, condenser and UPE filter cleaned, refrigerant checked and found normal, and both AC units restarted and tested successfully. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan
841 | Sirti-WAN-R3-Ticket-801 | NA | 2026-09-09 | P060-ENC02-CE-DGME-02 P060-ENC185-CE-DGME-01 | Arif | Link Fluctuating | WAN Link Fluctuating | QNBN Link Fluctuating |  | Zone 74 | 25.384331° 51.50058° | Outside Doha | P3 - Medium | 2026-09-09 12:40 | 2026-09-09 12:49 | 9.1167 | 2026-09-09 14:28 | 2026-09-09 14:29 | 1.1833 | 108.8833 | Link is auto restored before FLM reaching site | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
842 | Sirti-WAN-R3-Ticket-802 | NA | 2026-09-09 | P023C2-ENC43-CE-01 | Sanket | Link Down | Link Down | LAN Link down |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P3 - Medium | 2026-09-09 16:08 | 2026-09-09 16:17 | 9 | 2026-09-09 16:26 | 2026-09-09 16:28 | 1.3667 | 19.9667 | Link is auto restored before FLM reaching site | Completed | Non-maintainer | No Node Down | N/A | Alarm Cleared
843 | Sirti-WAN-R3-Ticket-803 | NA | 2026-09-09 | P011-ENC58-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | UPS issue |  | Zone 49 | 25.2273162° 51.5921766° | Outside Doha | P2 - High | 2026-09-09 19:02 | 2026-09-09 19:06 | 4 | 2026-09-09 19:45 | 2026-09-09 19:52 | 6.55 | 50.1167 | After Resetting the UPS, the issue was resolved | Completed | Non-maintainer | Defect | UPS | Device Restored | Irshad/Ghulam
844 | Sirti-WAN-R3-Ticket-804 | NA | 2026-09-09 | P004-ENC43-UPE-02 P004-ENC43-CE-01 P023C2-ENC43-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | AC was operational, but not cooling |  | Zone 51 | 25.3374686° 51.3242872° | Outside Doha | P2 - High | 2026-09-09 20:53 | 2026-09-09 20:55 | 1.3333 | 2026-09-09 20:57 | 2026-09-09 20:58 | 1.1833 | 5 | MCB tripped during AC troubleshooting. | Completed | Non-maintainer | Planned Activity | N/A | Device Restored | Khader
845 | Sirti-WAN-R3-Ticket-805 | 4547 | 2026-09-10 | P028C2-ENC07-UPE-02 P028C2-ENC07-CE-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | NO power at WAN cabinet |  | Zone 06 | 25.2827572° 51.5448455° | Inside Doha | P2 - High | 2026-09-10 04:17 | 2026-09-10 04:22 | 5 | 2026-09-10 04:55 | 2026-09-10 05:18 | 23.4833 | 61.45 | FLM switched on tripped CB at FP | Completed | Maintainer | N/A | N/A | Device Restored | Hicham
846 | Sirti-WAN-R3-Ticket-806 | 4554 | 2026-09-10 | 22FEB-ENC25-UPE-02 | Arif | CPU temperature too High | High Temperature | Relay was Damage |  | Zone 51 | 25.338322° 51.449241° | Outside Doha | P3 - Medium | 2026-09-10 08:09 | 2026-09-10 08:17 | 7.7833 | 2026-09-10 09:19 | 2026-09-10 09:21 | 2.7 | 72.1667 | The relay was damaged and has been replaced. The AC is now working properly. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
847 | Sirti-WAN-R3-Ticket-807 | 4569 | 2026-09-10 | P007C7P1-ENC06-UPE-01 | Arif | Temperature higher than Upper threshold | High Temperature | condenser fan and capacitor is faulty |  | Zone 55 | 25.249° 51.471° | Outside Doha | P3 - Medium | 2026-09-10 13:30 | 2026-09-10 13:42 | 11.8333 | 2026-09-10 15:30 | 2026-09-10 15:38 | 7.7833 | 127.6167 | Replaced the condenser fan and 5 µF capacitor with new ones. Also cleaned the AC filter | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khader
848 | Sirti-WAN-R3-Ticket-808 | 4568 | 2026-09-10 | P060-ENC02-CE-DGME-02 P060-ENC185-CE-DGME-01 | Arif | Link Down | WAN Link Down (Port Te 1/28 is down from both end) | The SFP is overheating because the AC is not cooling properly |  | Zone 74 | 25.384331° 51.50058° | Outside Doha | P3 - Medium | 2026-09-10 13:28 | 2026-09-10 13:32 | 4.2 | 2026-09-10 16:03 | 2026-09-10 16:13 | 10 | 164.8167 | The SFP was overheating because the AC was not cooling properly. The AC filter and unit were cleaned | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Khader
849 | Sirti-WAN-R3-Ticket-809 | NA | 2026-09-10 | P011-ENC58-CE-01 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity to replace faulty UPS batteries and cooling fans |  | Zone 49 | 25.2273162° 51.5921766° | Outside Doha | P2 - High | 2026-09-10 19:18 | 2026-09-10 19:19 | 1.0333 | 2026-09-10 19:29 | 2026-09-10 19:30 | 0.98333 | 11.5833 | Planned activity to replace faulty UPS batteries and cooling fans | Completed | Non-maintainer | Planned Activity | N/A | Device Restored | Ghulam
850 | Sirti-WAN-R3-Ticket-810 | 4572 | 2026-09-11 | CRR-ENC46-CE-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device down during troubleshooting AC issue |  | Zone 50 | 25.22608° 51.57875° | Outside Doha | P2 - High | 2026-09-11 04:19 | 2026-09-11 04:20 | 1.25 | 2026-09-11 04:19 | 2026-09-11 04:28 | 8.9667 | 8.9667 | Device down during troubleshooting AC issue | Completed | Non-maintainer | Planned Activity | N/A | Device Restored | Eric
851 | Sirti-WAN-R3-Ticket-811 | NA
852 | Sirti-WAN-R3-Ticket-812 | NA
853 | Sirti-WAN-R3-Ticket-813 | NA
854 | Sirti-WAN-R3-Ticket-814 | NA
855 | Sirti-WAN-R3-Ticket-815 | NA
856 | Sirti-WAN-R3-Ticket-816 | NA
857 | Sirti-WAN-R3-Ticket-817 | NA

## Legend
Maintainer | N/a | N/a | Maintainer | N/a | N/a
Non-maintainer | Access | no keys, police not allow | Non-maintainer | Access | no keys, police not allow
| Environmental | flooding, dust storm |  | Environmental | flooding, dust storm
| 3rd party | car crash, Bin omran contractor damage |  | 3rd party | car crash, Bin omran contractor damage